## q_Projects_Planned_Proposed
Midwest ISO Project Database - Project Table 8/03/2006 | [5 empty] | This is NOT Appendix A
PrjID | Prj Rec Date | Owner PrjID | Region | Rep Source | Project Name | Project Description | State | State2 | State2 frac | Need Summary | Project File | Budget Status | Reg Approvals | Delay Risk | Construction | Alternatives | Proj One-line | Idev file | Est MISO TO Cost | Funding Entity | Cost Resp MISO | Comments | Last Change | Project Doc | Submit Date | Review Date | Adequate Doc | Approve Date | Endorse Date | Cancellation Reason | App A | Need Date | Need Driver | Allocation Cat
90 | 2005-07-11 | 69 | N-ITWG | ALT | Emery-Lime Crk 161kV, Ckt 2 | Emery - Lime Creek 161 ckt 2, Sum rate 326 | IA |  |  | Contingency O.L. for many contingencies. | MISO_Lime Creek-Emery 161.doc | Pending | Pending |  | 0 | [12 empty] | 2003-06-25 |  |  | Y |  |  | Excluded
589 | 2006-03-10 |  | N-ITWG | ALT | Timber Crk-Highland Acres New 161kV | Timber Creek - Highland Acres (new) 161 kV line | IA |  |  | Replacing old 115 kV line in poor shape |  | Approved | Not Required | Low | [8 empty] | ALTW - Ken Leier | The new Highland Acres substation is being installed and fed from Timber Creek. But it is being built for 161 kV as it is along a route from Timber Creek between Fernald and Marshalltown which is 115 kV (poor condition line). But eventually it is planned to rebuild this line to 161 kV which will include this Highland Acres - Timber Creek section of line. So it is strictly benefiting the load serving purposes today, but will be regionally beneficial "tomorrow." It also would not show up on your present day contingency analysis. | [6 empty] | Y |  |  | Not Shared
746 | 2005-07-11 |  | N-ITWG | ALT | Huxley Ind. 69 kV 9.6 MVAR Cap | Huxley Industrial 69 kV 9.6 MVAR Capacitor | IA |  |  | Loss of Huxley Xfmr |  |  |  |  | 100 | [15 empty] | Y
1032 | 2005-09-08 |  | N-NM | ALT | Magnolia 161-69 kV transformer | Magnolia 161-69 kV transformer | MN | [23 empty] | Y
1035 | 2005-01-18 |  | N-ITWG | ALT | Wyoming 161/69 kV transformer | Wyoming 161/69 kV transformer | IA |  |  | Local load serving. Putting some 34.5 kV load onto the 69 kV system. | [20 empty] | Y
1141 | 2005-11-18 | G270 |  | ALTW | G270, 37579-01 |  | MN |  |  | http://www.midwestiso.org/plan_inter/documents/Adrian_MN_Generation_Study.pdf | [14 empty] | 2002-12-09 | [5 empty] | Y | 2003-05-01
1147 | 2005-11-18 | G298 |  | ALTW | G298, 37061-02 | Net: The Transmission Owner shall install a new 161kV line breaker on the Triboji- Wisdom Line and a new 161kV transformer breaker located on the existing #1 Triboji 161/69kV transformer and are shown in Exhibit A2.. Int: Generator shall construct a 161/34kV substation consisting of 161kV breaker, 161/34kV transformer, 34kV breakers and a 161kV line from (Bob what is name of Customer sub?) to the dead-end tower at the IPL Triboji substation. | IA |  |  | www.midwestiso.org/plan_inter/documents/G298_R2_Report.zip | [13 empty] | http://www.midwestiso.org/plan_inter/documents/G298_Facility_Report2.pdf | 2003-02-11 | [5 empty] | Y | 2006-12-31
1204 | 2006-01-31 |  | N-NM | ALTW | Adams-Rochester 161 kV line termination upgrade | Replace disconnect jumpers at Adams on Adams-Rochester 161 kV line | MN |  |  | TSR 76288610, A254 system impact study | [14 empty] | 2006-02-10 | [5 empty] | Y |  |  | Service
77 | 2005-07-11 | 54 | C-CSILL | Ameren | Callaway-Franks 345 kV Line | Callaway - Franks 345 kV line - New 345 kV line | MO |  |  | Project needed to relieve Bland-Franks 345 kV line | AMRN_MPDCalFrksRev2.doc | Approved | Obtained | Low | 20% | [12 empty] | 2003-06-25 |  |  | Y |  |  | Excluded
78 | 2006-03-17 | 55 | C-CSILL | Ameren | Jefferson City Area Development | Moreau - Apache Flats 161 kV line, Loose Creek - Jefferson City 345 kV line, Jefferson City 345/161kV Transformer | MO |  |  | Project needed to relieve Jefferson City area 161/69 kV transformers and 69 kV lines, Overton 345/161 kV transformer, and Montgomery-Guthrie 161 kV line. Will also improve area voltages. | AMRN_MPDJeffCtyArea Rev1.doc | Approved | Not Required | Medium | 0% | [7 empty] | Ameren - C Stepanek |  |  |  |  | 2003-06-25 |  |  | Y |  |  | Excluded
143 | 2006-03-17 | 121 | C-CSILL | Ameren | Cahokia-Pinckneyville-1 230 kV | Cahokia - N. Coulterville section of Cahokia-Pinckneyville-1 230 kV - Increase ground clearance | IL |  |  | Increase capability to support additional imports into AmerenUE, as required by the MO Public Service Commission |  | Approved | Not Required | Low | [8 empty] | Ameren - C Stepanek |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
144 | 2006-03-17 | 122 | C-CSILL | Ameren | Crab Orchard - Marion South 138 kV | Crab Orchard - Marion South 138 kV - Reconductor line | IL |  |  | Increase capability to support outage of W Frankfort-Shawnee 345 kV and enable the deliverability of Marion and Grand Tower plants in southern IL |  | Budgeted | Not Required | Low | [8 empty] | Ameren - C Stepanek |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
149 | 2006-03-17 | 127 | C-CSILL | Ameren | Mason-Sioux-7 345 kV | Mason-Sioux-7 345 kV - Breaker addition at Mason | MO |  |  | Project needed to maintain the Mason 345/138 kV #1 transformer in-service for the outage of the Mason-Sioux 345 kV line |  | Budgeted | Not Required | Low | [8 empty] | Ameren - C Stepanek |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
151 | 2005-07-11 | 129 | C-CSILL | Ameren | Buck Knob-Dupo Ferry-1 138 kV | Buck Knob-Dupo Ferry-1 138 kV - Reconductor line | IL |  |  | Replace old conductor |  | Budgeted | Not Required | [8 empty] | Branches with multiple status ??? Duplicate Project 83? | [8 empty] | Y |  |  | Share
152 | 2005-07-11 | 130 | C-CSILL | Ameren | Big River-Rockwood 138 kV | Big River-Rockwood 138 kV - Construct new line | MO |  |  | Project needed to serve area loads for double-circuit tower outages |  | Budgeted | Not Required | [17 empty] | Y |  |  | Share
153 | 2006-03-17 | 131 | C-CSILL | Ameren | Central-Watson-1 138 kV | CEE Tap - Watson section of Central-Watson-1 138 kV - Reconductor line | MO |  |  | Project needed to maintain import capability into AmerenUE |  | Approved | Not Required | Low | [8 empty] | Ameren - C Stepanek | [7 empty] | Y |  |  | Not Shared
155 | 2006-03-17 | 133 | C-CSILL | Ameren | Joachim 345/138 kV | Joachim 345/138 kV - New Substation | MO |  |  | Project needed to relieve Tyson 345/138 kV transformers and maintain import capability into AmerenUE | Joachim 345-138 kV Substation Addition.doc | Budgeted | Not Required | Low | 0% | A Dupo area 345/138 kV substation was briefly considered to relieve the Tyson transformers, but this option is considerably more expensive and less effective than the recommended Joachim option. | [6 empty] | Ameren - C Stepanek |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
707 | 2006-03-17 |  | C-CSILL | Ameren | Adair 161/69 kV Substation | Adair 161/69 kV Substation - Install 161 kV Breaker for Thomas Hill Line outage | MO |  |  | Project needed to maintain Adair voltages for the outage of the Thomas Hill-Adair 161 kV line |  | Approved | Not Required | Low | UC | [7 empty] | Ameren - C Stepanek |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
708 | 2006-03-17 |  | C-CSILL | Ameren | Casey-Breed 345 kV | Casey-Breed 345 kV Line - Reconductor river crossing | IL |  |  | IL Commerce Commission required |  | Approved | Not Required | Low | [8 empty] | Ameren - C Stepanek |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
710 | 2005-07-11 |  | C-CSILL | Ameren | Kinmundy-Salem 138 kV | Kinmundy-Salem 138 kV - Increase ground clearance | IL |  |  | Increase capability for the outage of Xenia-Mt Vernon 345 kV |  | Budgeted | Not Required | [14 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
711 | 2006-03-17 |  | C-CSILL | Ameren | Wood River-Gillespie 138 kV | Wood River-Gillespie 138 kV - Reconductor | IL |  |  | IL Commerce Commission required |  | Approved | Not Required | Low | [8 empty] | Ameren - C Stepanek |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
712 | 2006-03-17 |  | C-CSILL | Ameren | Mason 345/138 kV Substation | Labadie-Mason-3 345 kV Terminal equipment replacement | MO |  |  | Increase capability for the outage of Mason-Labadie-4 345 kV |  | Budgeted | Not Required | Low | [8 empty] | Ameren - C Stepanek |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
715 | 2005-07-11 |  | C-CSILL | Ameren | Wildwood-Gray Summit-1 138 kV | Wildwood-Gray Summit-1 138 kV - Reconductor line | MO |  |  | Increased capacity needed for double-circuit tower outage of Labadie-Tyson 345 kV lines |  | Budgeted | Not Required | [10 empty] | Wildwood - Eatherton - Babler tap - Gray Summit 138 kV line (additional taps in model) |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
716 | 2005-07-11 |  | C-CSILL | Ameren | Wildwood-Gray Summit-2 138 kV | Wildwood-Gray Summit-2 138 kV - Reconductor line | MO |  |  | Increased capacity needed for double-circuit tower outage of Labadie-Tyson 345 kV lines |  | Budgeted | Not Required | [10 empty] | Wildwood - Eatherton - Babler tap - Gray Summit 138 kV line (additional taps in model) |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
717 | 2005-07-11 |  | C-CSILL | Ameren | Conway-Tyson-3 138 kV | Conway-Orchard Gardens section of Conway-Tyson-3 138 kV - Increase ground clearance | MO |  |  | Increased capacity needed for double-circuit tower outage of Labadie-Mason 345 kV lines |  | Budgeted | Not Required | [14 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
718 | 2005-07-11 |  | C-CSILL | Ameren | Conway-Tyson-4 138 kV | Conway-Orchard Gardens section of Conway-Tyson-4 138 kV - Increase ground clearance | MO |  |  | Increased capacity needed for double-circuit tower outage of Labadie-Mason 345 kV lines |  | Budgeted | Not Required | [14 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
719 | 2006-03-17 |  | C-CSILL | Ameren | Labadie Plant | Labadie Plant - Replace 2-345 kV Breakers | MO |  |  | Overstressed circuit breakers |  | Budgeted | Not Required | Low | [7 empty] | Related to Prairie State Plant | Ameren - C Stepanek |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Service
720 | 2005-07-11 |  | C-CSILL | Ameren | Page 138/34 kV Substation | Page 138/34 kV Substation - Replace 3-138 kV Breakers | MO |  |  | Overstressed circuit breakers |  | Budgeted | Not Required | [14 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
721 | 2005-07-11 |  | C-CSILL | Ameren | Wildwood 345/138 kV Substation | Wildwood 345/138 kV Substation - Add 2-345 kV Breakers | MO |  |  | Maintain Wildwood 345/138 kV transformer in service for double-circuit outage of Labadie-Mason 345 kV lines |  | Budgeted | Not Required | [17 empty] | Y |  |  | Not Shared
783 | 2005-07-11 |  | C-CSILL | Ameren | Robinson-Marathon 138 kV Substation | Robinson-Marathon 138 kV Substation - Increase 18 MvarCapacitor bank to 36 Mvar | IL |  |  | Increase local voltage support for conditions with Hutsonville generation off |  | Budgeted | Not Required | [17 empty] | Y |  |  | Not Shared
856 | 2005-07-11 |  | C-CSILL | Ameren | Osage 138 kV Substation | Osage 138 kV Substation - Replace bus conductor in bus #1 and line to Eldon | MO |  |  | Increased capacity needed for outage of Montgomery-Overton-5 345 kV | [20 empty] | Y |  |  | Not Shared
857 | 2005-07-11 |  | C-CSILL | Ameren | Rush Island-Joachim 345 kV Line | Rush Island-Joachim 345 kV - Replace terminal equipment at Rush Island | MO |  |  | Prairie State Generation Addition | [20 empty] | Y |  |  | Not Shared
858 | 2005-07-11 |  | C-CSILL | Ameren | Sioux-Huster-1 138 kV | Sioux-Huster-1 138 kV - Increase ground clearance on 6 miles of 795 kcmil ACSR | MO |  |  | Increased capacity needed for double-circuit tower outage of Sioux-Belleau 345 kV and Sioux-Huster-3 138 kV. | [20 empty] | Y |  |  | Not Shared
859 | 2005-07-11 |  | C-CSILL | Ameren | Central-Watson-1 138 kV | Central-Watson-1 138 kV - Reconductor 5.1 miles 954 kcmil ACSR between Central and Twr. 55 | MO |  |  | Increased capacity needed for outage of Sioux-Roxford-5 345 kV | [20 empty] | Y |  |  | Not Shared
1233 | 2006-03-17 |  | C-CSILL | Ameren | Cahokia-Ashley-2 138 kV | Replace bus conductor and retap CTs | MO | [15 empty] | Curt Stepanek | [7 empty] | Y |  |  | Not Shared
1235 | 2006-03-17 |  | C-CSILL | Ameren | Fredericktown-AECI Fredericktown | Increase ground clearance on 12 miles | MO |  |  | Safety | [12 empty] | Curt Stepanek | [7 empty] | Y |  |  | Not Shared
1237 | 2006-03-17 |  | C-CSILL | Ameren | Cambell-Euclid-Page 138 kV | Rebuild 5.25 miles dbl-ckt. 138 kV | MO |  |  | Long-term solution for metro area | [12 empty] | Curt Stepanek | [7 empty] | Y |  |  | Share
1238 | 2006-03-17 |  | C-CSILL | Ameren | GM-Point Prairie 161 kV to AECI Enon Sub. | Extend 1 mile of 161 kV to AECI Enon Substation | MO |  |  | Support for Wentxville area | [12 empty] | Curt Stepanek | [7 empty] | Y |  |  | Not Shared
1240 | 2006-03-17 |  | C-CSILL | Ameren | Reconductor Sioux-Huster-1 and -3 138 kV | Reconductor 15 miles of Sioux-Huster-1 and 13 miles of Sioux-Huster-3 | MO |  |  | Safety | [12 empty] | Curt Stepanek | [7 empty] | Y |  |  | Not Shared
141 | 2006-03-17 | 119 | C-CSILL | AmerenCILCO | Duck Creek-Tazewell 345 kV | Duck Creek-Tazewell 345 kV - Convert bus duct to overhead | IL |  |  | Capital project to eliminate maintenance issue |  | Not Budgeted | Not Required | [9 empty] | Ameren - C Stepanek |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
874 | 2005-07-11 |  | C-CSILL | AmerenCILCO | East Springfield 138/69 kV Substation | East Springfield 138/69 kV Substation - Replace terminal equipment | IL |  |  | Conversion to Ameren rating practices | [20 empty] | Y |  |  | Not Shared
875 | 2005-07-11 |  | C-CSILL | AmerenCILCO | Kickapoo 138/69 kV Substation | Kickapoo 138/69 kV Substation - Replace terminal equipment | IL |  |  | Conversion to Ameren rating practices | [20 empty] | Y |  |  | Not Shared
876 | 2005-07-11 |  | C-CSILL | AmerenCILCO | Tazewell 345/138 kV Substation | Tazewell 345/138 kV Substation - Replace 2000 A terminal equipment with 3000 A on line to Powerton | IL |  |  | Phase II regulatory obligation with Illinois Commerce Commission for Ameren's acquisition of CILCO. Project increases import capability to CILCO. Conversion to Ameren rating practices. | [13 empty] | Phase II regulatory obligation with Illinois Commerce Commission for Ameren's acquisition of CILCO. Project increases import capability to CILCO. | [6 empty] | Y |  |  | Share
150 | 2006-03-17 |  | C-CSILL | AmerenIP | Prairie State Power Plant transmission outlet | Establish a new Prairie State 345 kV switchyard including a 6-position breaker and ½ bus arrangement to accommodate 2 generating units and 4-345 kV outlet lines with 9-345 kV circuit breakers. Tap the existing Baldwin-Stallings 345 kV line 4531 "in and out" and build 7.5 miles of double-circuit 3000 A summer emergency capability line to the switchyard. Tap the existing Baldwin-Mt. Vernon 345 kV line 4541 "in and out" and build 1.5 miles of double-circuit 3000 A summer emergency capability line to the switchyard. At the Baldwin 345 kV switchyard, replace 9-345 kV circuit breakers that would be overstressed as a result of the Prairie State development. Also install 3-345 kV circuit breakers for a new Baldwin-Rush Island 345 kV line and a new connection for the Baldwin 345/138 kV transformer. Build a new 26 mile 345 kV 3000 A summer emergency capability line from Baldwin to Rush Island. | IL |  |  | Project needed to connect and provide partially deliverability of Prairie State generation to the MISO footprint. | Ameren Prairie State Plant trans outlet.doc | Pending | Pending | Medium | 0% | Several connection options were considered, including radial Prairie State-Baldwin 345 kV lines, but the proposed arrangement satisfies both powerflow and stability issues better than the other options. | [5 empty] | Total project cost is $77 million. MISO reported generator related facilities | Curt Stepanek |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Service
724 | 2006-03-17 |  | C-CSILL | AmerenIP | Rising-Bondville Rt. 10 138 kV line | Rising-Bondville 138 kV - Install 138 kV breaker at Bondville, construct 3 miles new 138 kV line | IL |  |  | 138 kV line extension needed to supply 138/69 kV transformer in Champaign IL area |  | Approved | Pending | Medium | [8 empty] | Ameren - C Stepanek |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
725 | 2006-03-17 | 725 | C-CSILL | AmerenIP | LaSalle Area Development | N. LaSalle-N. Ottawa 138 kV - 20 miles new line, 138 kV breaker addition at N. LaSalle, new 3 terminal ring bus at N.Ottawa. N.Ottawa-Ottawa 138 kV - 2 new 138 kV breakers, 2.5 miles new line. N. Ottawa-Wedron 138 kV - 8 miles new line | IL |  |  | 138 kV line extension needed to supply 138/34 kV transformer in LaSalle IL area |  | Approved | Required | Medium | [8 empty] | Ameren - C Stepanek |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
726 | 2005-07-11 | 725 | C-CSILL | AmerenIP | LaSalle Area Development | Ottawa-Wedron Fox River 138 kV - Construct 14 miles new 138 kV line, 1 new 138 kV breaker at Ottawa | IL |  |  | 138 kV line extension needed to supply 138/34 kV transformer in LaSalle IL area |  |  | Required | [9 empty] | Ameren - J Sullivan |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
728 | 2006-03-17 |  | C-CSILL | AmerenIP | Wood River-Roxford 1502 138 kV line | Wood River-Roxford 1502 138 kV line - Reconductor | IL |  |  | Project needed to increase AmerenUE import FCITC for the outage of the Wood River-Roxford 138 kV line 1506 |  | Approved | Not Required | Low | [8 empty] | Ameren - C Stepanek | [7 empty] | Y |  |  | Share
732 | 2006-03-17 |  | C-CSILL | AmerenIP | S. Bloomington-State Farm 138 kV | S. Bloomington-State Farm 138 kV - Reconductor | IL |  |  | Project needed to increase capability for outage of Brokaw-Bloomiongton 138 kV line #2 |  | Approved | Not Required | [9 empty] | Ameren - C Stepanek | [7 empty] | Y |  |  | Not Shared
734 | 2006-03-17 | 734 | C-CSILL | AmerenIP | Washington Street Substation Development | Washington Street Sub - Install ring bus and split S.Bloomington to Raab Rd. 138 kV Line 1326, tap 138 kV Line 1364. 138 kV Line 1364 - Reconductor from S. Bloomington Substation to Tower 512 | IL |  |  | Project needed to increase support to Bloomington area load and west side of Bloomington load |  | Budgeted | Not Required | [9 empty] | Ameren - C Stepanek | [7 empty] | Y |  |  | Service
736 | 2006-03-17 |  | C-CSILL | AmerenIP | W. Tilton 138 kV Substation | W. Tilton 138 kV Substation - Install 138 kV breaker | IL |  |  | Breaker needed to split existing line and provide 2nd 138 kV supply to 2nd W Tilton 138/69 transformer |  | Not Budgeted | Not Required | [9 empty] | Ameren - C Stepanek | [7 empty] | Y |  |  | Not Shared
737 | 2006-03-17 |  | C-CSILL | AmerenIP | Bluff City 138 kV Substation | Bluff City 138 kV Substation - Install 138 kV breaker | IL |  |  | Breaker needed to split existing line and provide 2nd 138 kV supply to 2nd Bluff City 138/69 transformer |  | Not Budgeted | Not Required | [9 empty] | Ameren - C Stepanek | [7 empty] | Y |  |  | Not Shared
738 | 2006-03-17 |  | C-CSILL | AmerenIP | Latham-Lanesville 138 kV Line | 138 kV Line 1342C tap - Line 1342A - Reconductor structure 423 to 467A | IL |  |  | Project needed to provide deliverability to IPP generator (Turris Coal aka Cornbelt) |  | Approved | Not Required | Low | [8 empty] | Ameren - C Stepanek |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
739 | 2006-03-17 |  | C-CSILL | AmerenIP | Franklin County Power Plant Connection | Franklin County Power Plant Connection - Tap 345 kV Line 4561 Tap, and Install new 345 kV ring bus | IL |  |  | Project needed to connect IPP generation (Enviropower) |  | Not Budgeted | Required | [9 empty] | Ameren - C Stepanek | [7 empty] | Y |  |  | Service
865 | 2006-03-17 |  | C-CSILL | AmerenIP | Havana-Monmouth 138 kV River Crossing | Havana-Monmouth 138 kV Line 1362 - Rebuild river crossing | IL |  |  | Conversion to Ameren rating practices | [12 empty] | Curt Stepanek | [7 empty] | Y |  |  | Not Shared
866 | 2005-07-11 |  | C-CSILL | AmerenIP | Latham 345/138 kV Substation | Latham 345/138 kV Substation - Install 138 kV breaker for 'in-out' taps to 138 kV Line 1342, construct 0.38 miles 138 kV line for 'in-out' connections | IL |  |  | Increased capacity for Duck Creek-Tazewell 345 kV outage; also for Havana, Meredosia, and Duck Creek deliverability | [20 empty] | Y |  |  | Not Shared
869 | 2005-07-11 |  | C-CSILL | AmerenIP | Sidney-Mira Tap 138 kV | Sidney-Mira Tap 138 kV - Reconductor 2 miles 795 kcmil ACSR | IL |  |  | Increased capacity for outage of Clinton unit and S.W. Campus-Windsor-Sidney 138 kV | [20 empty] | Y |  |  | Not Shared
870 | 2005-07-11 |  | C-CSILL | AmerenIP | Sidney-Paxton 138 kV | Sidney-Paxton 138 kV - Reconductor 18 miles of 350 kcmil Cu | IL |  |  | Increased capacity needed for outage of Clinton unit at Sidney-Rantoul Junction 138 kV | [20 empty] | Y |  |  | Share
872 | 2005-07-11 |  | C-CSILL | AmerenIP | Mahomet-Champaign 138 kV Line 1592 | Mahomet-Champaign 138 kV Line 1592 - Reconductor 1.55 miles of 477 kcmil ACSR from Mahomet Substation to Twr. 29 | IL |  |  | Conversion to Ameren rating practices | [20 empty] | Y |  |  | Not Shared
873 | 2005-07-11 |  | C-CSILL | AmerenIP | Baldwin Plant 345 kV Switchyard | Replace 6-345 kV breakers with breakers having 3000 A continuous capability | IL |  |  | Prairie State Generation Addition | [20 empty] | Y |  |  | Share
1234 | 2006-03-17 |  | C-CSILL | AmerenIP | Havana, South-Mason City, West 138 kV | Increase ground clearance on 18.4 miles | IL |  |  | System upgrade for Clinton unit off & line outage | [12 empty] | Curt Stepanek | [7 empty] | Y |  |  | Not Shared
1236 | 2006-03-17 |  | C-CSILL | AmerenIP | Stallings-Prairie State Plant 345 kV | Replace 2000 A terminal equipment with 3000 A equipment | IL |  |  | Generation Addition | [12 empty] | Curt Stepanek | [7 empty] | Y |  |  | Not Shared
1239 | 2006-03-17 |  | C-CSILL | AmerenIP | Normal, East-Brokaw 138 kV | Replace 600 A terminal equipment at Normal, East Sub. With 1200 A | IL |  |  | Conversion to Ameren rating practices | [12 empty] | Curt Stepanek | [7 empty] | Y |  |  | Not Shared
1048 | 2005-11-18 | G014 |  | ATC | G014, 36465-01 | Net: The Transmission Service Requests associated with this proposed facility are MISO OASIS #72856710, 72856700, 72807215 and #72807208.. Int: Six new breakers connecting the generator step up transformers to the Port Washington substation bus must be specified as a minimum of 2-cycle, 63kA, gang operated. Substation reconfiguration at the Port Washington substation. | WI |  |  | Required for generator interconnection request | [13 empty] | http://www.midwestiso.org/plan_inter/documents/G014_Report.pdf | 1999-11-01 | [5 empty] | Y | 2005-07-01
1075 | 2005-11-18 | G044 |  | ATC | G044, 36705-01 |  | WI |  |  | Required for generator interconnection request | [13 empty] | http://oasis.midwestiso.org/documents/ATC/GIC007%20Study%20Report.pdf | 2000-06-28 | [5 empty] | Y | 2005-06-01
1077 | 2005-11-18 | G051 |  | ATC | G051, 36760-01 |  | WI |  |  | http://www.midwestiso.org/plan_inter/documents/GIC012A_prel_restudy_stability_report_phaseII.pdf | [13 empty] | http://oasis.midwestiso.org/documents/ATC/GIC012A%20Study%20Report.pdf | 2000-08-22 | [5 empty] | Y | 2009-01-01
1083 | 2005-11-18 | G063 |  | ATC | G063, 36825-01 |  | WI |  |  | Required for generator interconnection request | [13 empty] | http://oasis.midwestiso.org/documents/ATC/GIC015%20Study%20Report.pdf | 2000-10-26 | [5 empty] | Y
1095 | 2005-11-18 | G093 |  | ATC | G093, 37004-01 |  | WI |  |  | http://oasis.midwestiso.org/documents/ATC/GIC027_Impact_Report_Rev1.pdf | [13 empty] | http://oasis.midwestiso.org/documents/ATC/GIC027_Facilities_Study_Report.pdf | 2001-04-23 | [5 empty] | Y | 2008-05-01
1097 | 2005-11-18 | G096 |  | ATC | G096, 37055-01 | Net: The Transmission Service Requests associated with this proposed facility are MISO OASIS #75004950 and #75004952. Already in the model. Int: New East Campus-Walnut 69kV Circuit; East Campus Bus Reconfiguration; Walnut Bus Reconfiguration | WI |  |  | Required for generator interconnection request | [13 empty] | http://oasis.midwestiso.org/documents/ATC/GIC029-49%20Final%20Report%20Rev%201.pdf | 2001-06-13 | [5 empty] | Y | 2005-03-07
1098 | 2005-11-18 | G103 |  | ATC | G103, 37062-04 | Net: Already in the model. Major transmission system upgrades would be required to address the identified power flow issues. Possible solutions include line terminal upgrades, increased line clearances, increasing the rating of existing transmission lines and the addition of new transmission lines.. Int: Already in the model | WI |  |  | http://oasis.midwestiso.org/documents/ATC/GIC034%20System%20Impact%20Study%20report.pdf | [13 empty] | http://oasis.midwestiso.org/documents/ATC/GIC034%20System%20Facility%20Study%20Report.pdf | 2001-06-20 | [5 empty] | Y | 2005-06-01
1107 | 2005-11-18 | G144 |  | ATC | G144, 37187-02 | Net: 1) Arrowhead-Weston 345 kV transmission line project, 2) the Morgan-Werner West 345 kV transmission line project, and 3) a 345 kV transmission line from the Weston substation to a new Central Wisconsin substation located on the Morgan–Werner West 345 kV transmission line.. Int: NA | WI |  |  | http://oasis.midwestiso.org/documents/ATC/GIC044%20System%20Impact%20Study%20report.pdf | [13 empty] | http://oasis.midwestiso.org/documents/ATC/GIC044%20Facility%20Study%20Report.pdf | 2001-10-23 | [5 empty] | Y | 2007-06-01
1112 | 2005-11-18 | G160 |  | ATC | G160, 37225-01 |  | WI |  |  | Required for generator interconnection request | [13 empty] | http://oasis.midwestiso.org/documents/ATC/ic029-49summary.pdf | 2001-11-30 | [5 empty] | Y | 2005-03-07
1129 | 2005-11-18 | G240 |  | ATC | G240, 37466-01 | Net: specific thermal impacts should be provided by the results of the TSR study for G240 (MISO_#75109302).. Int: Relocation of line D-104 to facilitate the Facility’s interconnection to the 69 kV system. Installation of new 69 kV 3-cycle breakers on D-104 at Lakefront, control cables, control/relays, foundation, carrier equipment, and switches as required at both Lakefront Substation and Revere Substation. | WI |  |  | http://www.midwestiso.org/plan_inter/documents/G240_System_Impact_Study_Report.pdf | [13 empty] | http://oasis.midwestiso.org/documents/ATC/G240%20Facility%20Study%20Report.pdf | 2002-07-29 | [5 empty] | Y | 2005-09-01
1174 | 2005-11-18 | G353 |  | ATC | G353, 37825-01 | Net: . Int: A single collection bus at 34.5 kV. A 345 /34.5 kV transformer, a ringbus to interconnect G335 to Forest Jct @ Arcadian 345 kV line. The Gen will have a 345 kV breker on the high side of the gen step up. | WI |  |  | Required for generator interconnection request | [13 empty] | http://oasis.midwestiso.org/documents/ATC/G353_G354_Facility_Study_Report.pdf. | 2003-07-23 | [5 empty] | Y | 2006-05-01
1175 | 2005-11-18 | G354 |  | ATC | G354, 37825-02 | Net: . Int: include a 160 MVA transformer, a 345 kV circuit breaker, a power factor compensation system sized and controlled appropriately for the MVAR needs of the 160 MW interconnection, plus all required relays and infrastructure to meet the requirements of a safe and reliable interconnection. In addition, Generator shall construct an individual 34.5 kV breaker on the low side of the generator step-up transformer, which breaker will be used to isolate its Facility. | WI |  |  | Required for generator interconnection request | [13 empty] | http://oasis.midwestiso.org/documents/ATC/G353_G354_Facility_Study_Report.pdf | 2003-07-23 | [5 empty] | Y | 2006-05-01
1 | 2005-07-11 | 1 | C-WUMS | ATC LLC | Arrowhead-Gardner Park 345 kV | Arrowhead - Gardner Park 345 kV line | WI | MN |  | Improved reliability and import capability, as well as extra stability at Weston; also required for Generator-Transmission interconnection G144 |  | Approved | Obtained | Low | 10% | [12 empty] | 2003-06-25 |  |  | Y |  |  | Excluded
2 | 2005-07-11 |  | C-WUMS | ATC LLC | Weston - Northpoint 115 kV reconductor | Reconductor Weston-Dewey Tap-Northpoint 115 kV line with 795 ACSR conductor. | WI |  | 0 | The Weston-Northpoint 115 kV circuit is presently a transmission service limiter as well as a line associated with significant redispatch costs to ATC. In 2002, Transmission Loading Relief incidents (TLRs) were called for the outage of the Weston-Rocky Run 345 kV on 34 days, whereas in 2003 they were called 36 times. Costs associated with generation redispatch to alleviate these limitations were $270,010 and $185,786 in the years 2002 and 2003 respectively. The Weston-Northpoint 115 kV circuit currently risks first-contingency overloads depending on the amount of Weston generation dispatched. The worst contingency is a trip of Weston generator #3. To accept the 500 MW IC044 (2008) transmission service request, Facility Study #75000492 identifies the reconductor of the Weston-Northpoint 115 kV line as an interim project until higher-voltage upgrades can be completed. This line is also identified for reconductor in Facility Study #75000549 for a total of 135 MW from a source in the WPS control area to the UPPCo control area by January of 2008. However, during the planned Gardner Park-Stone Lake 345 kV construction in 2006, the Weston-Rocky Run 345 kV line will be out of service. Thus, the timing of the reconductor of Weston-Northpoint-Rocky Run 115 kV line T-20 becomes more crucial and should be accelerated to an in-service date of mid 2006. | ATC Weston-Northpoint.doc | Approved | Not Required | Low | 0% | Alternatives to the reconductor of this line were considered (such as constructing new facilities) but were deemed infeasible due to cost differential, regulatory and/or time constraints. Several conductor types were identified as possible candidates for this reconductor: 477 ACSR at 300F clearance, 795 ACSR at 200F clearance, 795 ACSR at 300F clearance and 477 ACSR T2 at 200F clearance. | [5 empty] | Was previously ncluded in Arrowhead - Gardner Park 345 project | [5 empty] | 2003-06-25 |  |  | Y |  |  | Excluded
15 | 2006-07-05 | 9 | C-WUMS | ATC LLC | Plains-Stiles Double-Circuit Rebuild | Plains - Amberg - Stiles 138 kV line rebuild | WI |  |  | Improve reliability under contingency during high flows between Wisconsin and Upper Peninsula of Michigan. | ATC Plains-Amberg-Stiles.doc | Approved | Obtained | Low | 75% | [7 empty] | ATC - Wenchun Zhu |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
21 | 2005-07-11 | 10 | C-WUMS | ATC LLC | Metonga T-D interconnection | Venus-Metonga (was Crandon) 138 kV line | WI |  |  | Transmission-Distribution interconnection | ATC venus-plains 138.doc | Approved | Pending |  | 0% | [12 empty] | 2003-06-25 |  |  | Y |  |  | Share
22 | 2005-11-18 | 11 | C-WUMS | ATC LLC | Femrite-Sprecher new 138 kV; Sprecher-Reiner-Sycamore conversion to 138 kV | Femrite - Sprecher 138 (new), Sprecher - Reiner 138 (conversion), Reiner - Sycamore 138 (conversion), | WI |  |  | Improved reliability; accommodate West Campus cogen additions. The Femrite - Sycamore project is required to accommodate new generation in Dane County. In addition, the line will be used for load serving and was required to approve a Transmission Service request. | ATC femrite-sycamore 138.doc | Approved | Obtained | [10 empty] | This project is part of the East Madison (Dane County, Wisconsin) 138 kV loop. The project includes acquiring 4.0 miles of new right of way between Femrite and Sprecher. The existing 69 kV line from Sprecher to Reiner Road tap to Sycamore was built for 138 kV operation. However, it is currently being operated at 69 kV. This project includes converting the Sprecher – Sycamore line to 138 kV operation. The Femrite substation will be expanded to include a 138 kV bus and a 100 MVA, 138/69 kV transformer. A 1000-foot section of line from the Reiner Tap to Reiner will also need to be rebuilt for 138 kV operation. A 100 MVA, 138/69 kV transformer will be installed at Reiner Road. As part of the East Madison 138 kV loop project, the Kegonsa – McFarland – Femrite line will be converted to 138kV operation. This line will be rebuilt for 138kV operation by 2004, but operated at 69 kV between 2004 and 2006. |  |  |  | 2003-06-25 |  |  | Y |  |  | Excluded
62 | 2005-11-18 | 44 | C-WUMS | ATC LLC | Wien-McMillan 115 kV | Wien - Stratford - McMillan 115 ckt , Sum rate 202 | WI |  |  | The outage on the Arpin 138/115 transformer or the Arpin-Hume 115 kV line in 2005 results in overloads on Wien-Stratford-McMillan 115 kV lines as well as voltages below 90%at Hume, Wildwood and McMillan. |  | Approved | Not Required |  | 0% | [12 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
64 | 2005-07-11 | 46 | C-WUMS | ATC LLC | Kegonsa-McFarland-Femrite conversion to 138 kV | Kegonsa - McFarland -Femrite conversion to 138 kV | WI |  |  | Improved reliability and Generator-Transmission interconnection G035 & G072 | ATC Kegonsa-McFarland-Femrite conv 138.doc | Approved | Obtained | [14 empty] | 2003-06-25 |  |  | Y |  |  | Excluded
89 | 2006-07-05 | 67 | C-WUMS | ATC LLC | Mill Road 345/138 kV substation and transformer | Mill Road transformer - 345/138 ckt , Sum rate 500 | WI |  |  | To address as a first step (Phase I) system reliability issues concerning low voltages under normal system conditions and unacceptably low voltages and thermal overloads under single contingency conditions in the area of Jefferson, Washington and Waukesha Counties. This due primarily to high residential, commercial and light industrial load growth in the tri-county area. Eliminate the need to rely on the operation of Germantown and Concord power plants for voltage support. |  | NA. - project deferred to 2019 | NA - project deferred until 2018 | [9 empty] | ATC - Wenchun Zhu |  |  |  |  | 2003-06-25 |  |  | Y
101 | 2005-07-11 | 82 | C-WUMS | ATC LLC | Kelly-Whitcomb 115 kV uprate | Kelly - Whitcomb 115 ckt , Sum rate 241 | WI |  |  | Installation of Arrowhead-Gardner Park 345 kV line, G-T interconnection G144, and TSRs 75000492 and 75000549 require Line J-36 from the Kelly Substation to the Whitcomb Substation to have an increased current carrying capability. |  | Pending | Not Required |  | 0% | [12 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
102 | 2006-03-16 | 83 | C-WUMS | ATC LLC | Port Washington generator additions projects | Port Washington generator additions; Port Washington-Saukville, Port Washington-Range Line 138 kV rebuilds | WI |  |  | Generator-Transmission interconnection G014 & G093 |  | Pending | Pending | [9 empty] | ATC - Paul Hesse |  |  |  |  | 2003-06-25 |  |  | Y |  |  | Service
168 | 2005-07-11 | 146 | C-WUMS | ATC LLC | Werner West 345/138 kV transformer | Werner West transformer - 345/138 ckt , Sum rate 500 | WI |  |  | Generator-Transmission interconnection G144 |  | Approved | Obtained | Low | 0% | [15 empty] | Y |  |  | Excluded
171 | 2005-07-11 | 149 | C-WUMS | ATC LLC | Weston-Kelly 115 kV | Weston - Kelly 115 ckt , Sum rate 239 | WI |  |  | Generator-Transmission interconnection G144 |  | Approved | Not Required |  | 0% | [12 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
174 | 2005-07-11 | 152 | C-WUMS | ATC LLC | Canal-Dunn Road 138 kV | Canal - Dunn Road 138 ckt , Sum rate 400 | WI |  |  | Electricity demand in Door County has been growing at an aggressive rate. The 69 kV transmission system serving the northern portion of Door County is quickly reaching its capacity. In addition, most of the northern portion of the county, being served by a single line, is vulnerable to extended interruption of service if that single line suffered an extended outage. Without reinforcements in the near future, this system will be susceptible to facility overloads and unacceptably low voltages. The projects will provide significant voltage support, provide a second source, and provide additional transformation capacity to Northern Door County area. |  | Not Budgeted | Not Required | Low | 0% | [15 empty] | Y
175 | 2005-07-11 | 153 | C-WUMS | ATC LLC | Ellinwood-Sunset Point 138 kV | Ellinwood - Sunset Point 138 ckt , Sum rate | WI |  |  | Much of the area in the eastern portion of Winnebago County is served by the 69 kV transmission systems via Ellinwood or Sunset Point 138/69 kV substations. Studies conducted by Planning indicated that under certain generation pattern the Ellinwood 138/69 kV T1 transformer and Ellinwood-12th Ave 69 kV line would be overloaded by 18 % and 2 % respectively under the outage of Fitzgerald-Sunset Point 138 kV line in 2005 time frame. In addition, studies conducted by System Operations indicated that load curtailment would be required to mitigate system problems caused by the double contingency of Fitzgerald-Sunset Point 138 kV line and Neevin-Woodenshoe 138 kV line. The proposed project will address the potential transformer and line overloads, and provide operational/maintenance flexibility. The requested in-service date for this project is June 2007. |  | Not Budgeted | Not Required | Low | 0% | [15 empty] | Y |  |  | Excluded
177 | 2006-03-16 | 155 | C-WUMS | ATC LLC | Gardner Park-Central Wisconsin 345 kV line projects | Construct Gardner Park-Central Wisconsin 345 kV line and Construct new Central Wisconsin 345 kV substation | WI |  |  | Generator-Transmission interconnection G144 Wisconsin Public Service Corporation (WPS) is planning to construct a new 550 MW coal fired generator at their existing Weston power plant. This new generator (“Weston 4”) will be connected to the future Gardner Park 345 kV bus (on the Weston site). System Planning conducted analyses to ensure that Weston 4 can be operated without stability limitations and the output of Weston 4 can be delivered reliably. The analyses conducted show that the addition of Weston 4 will cause overloads and system instability if the existing transmission system in the area is not improved. In addition, there are other related factors that need to be considered in evaluating system improvement alternatives, including the impact of the planned Arrowhead-Gardner Park 345 kV transmission line, the load serving needs in the Wausau and Rhinelander areas and operating considerations. System Planning is proposing a project that not only addresses the system stability and delivery requirements of Weston 4, but also: 1) ensures that the 3,000 MW import capability target - one of the underlying needs for the Arrowhead-Gardner Park line - is not compromised, 2) ensures that the load serving needs in the Wausau and Rhinelander areas are not compromised, and 3) strengthens the transmission system between north-central and northeastern Wisconsin by creating a 345 kV path parallel to almost the entire length of the existing Rocky Run to North Appleton 345 kV line, currently the only 345 kV circuit that connects the transmission systems in north-central and northeastern Wisconsin, which improves the reliability of the system under a wider variety of multiple contingency conditions than other alternatives and thus, improving operating flexibility. | ATC Gardner Park-Central Wisconsin.doc | Approved | Pending | High | 0% | Alternative #1: Arrowhead-Stone Lake-Gardner Park and Gardner Park-Morgan 345 kV lines. Alternative #2: Arrowhead-Stone Lake-Gardner Park and a second Gardner Park- Rocky Run 345 kV line. Alternative #3: Arrowhead-Stone Lake-Gardner Park and Low Voltage (115 and 138 kV) Requirements. | [5 empty] | No increased risk | ATC - Paul Hesse | [7 empty] | Y |  |  | Service
333 | 2006-03-16 | newgrp12 | C-WUMS | ATC LLC | Hiawatha-Indian Lake conversion to 138 kV and Hiawatha-Pine River-Mackinac conversion to 138 kV | Construct Mackinac 138 kV substation (new Straits substation) - 2007 Relocate 69 kV Rexton tap to 69 kV Hiawatha-Pine River line (6909) - 2009 Relocate 69 kV Trout Lake tap to 69 kV Hiawatha-Pine River line (6909) - 2009 Construct Mackinac 138 kV substation additions (portions may be earlier for maintenance issues) - 2009 Rebuild Hiawatha-Pine River-Mackinac 69 kV to 138 kV - 2009 Construct 138 kV bus and install one 138/69 kV, 50 MVA transformers at Pine River - 2009 Convert rebuilt Hiawatha-Indian Lake circuit (operated at 69 kV) to 138 kV - 2009 Construct 138 kV ring bus at Hiawatha SS - 2009 Install 138 kV substation modifications at Indian Lake SS - 2009 | WI |  |  | Hiawatha-Pine River-Mackinac: condition of facilities, eliminate overloads and low voltages. Hiawatha-Indian Lake: age of facilities, condition of facilities, eliminate overloads and low voltages, eliminate transmission loading relief incidents in the Upper Peninsula of Michigan. |  | Pending | Not Required | High | 0% | No viable alternatives were considered for this project. | [5 empty] | Project has changed to provisional status | ATC - Paul Hesse |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
339 | 2005-07-11 | newgrp15 | C-WUMS | ATC LLC | Lake Mills Transmission-Distribution interconnection | Construct a Jefferson-Lake Mills-Stony Brook 138 kV line Uprate Rockdale to Jefferson 138 kV line Uprate Rockdale to Boxelder 138 kV line Uprate Boxelder to Stonybrook 138 kV line | WI |  |  | Lake Mills Transmission-Distribution request and improve low voltages under contingency in surrounding area. | P339 Lake Miles T-D.doc | Pending | Pending | Low | 0% | Option 1: Build a new London-Lake Mills-Jefferson line Option 2: Build a 345 kV Substation with 345/138 kV Transformation at North Randolph and radial 138 kV line from Jefferson to Lake Mills Option 3: Build a new Box Elder-Lake Mills-Jefferson 138 kV line | [11 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
341 | 2006-03-16 | newgrp19 | C-WUMS | ATC LLC | Rockdale-Mill Road 345 kV line projects | Construct Rockdale-Concord 345 kV line in parallel with existing 138 kV on existing double-width right-of-way. Construct a 345 kV bus and install a 345/138 kV, 500 MVA transformer at Concord. Convert Bark River-Mill Road 138 kV line to 345 kV. Construct a Concord-Bark River 345 kV line. Construct a 345 kV bus and install a 345/138 kV, 500 MVA transformer at Bark River | WI |  |  | Address low voltages under normal system conditions and unacceptably low voltages and thermal overloads under single contingency conditions in the areas of Jefferson, Washington and Waukesha Counties. This is due primarily to high residential, commercial and light industrial load growth in the tri-county area. Eliminate the need to run expensive Germantown and Concord generation units for voltage support. The Project will also improve west-east transfer capability with ATC system by 400 MW and reduce losses by over 20 MW. | P341 ATC Rockdale-Mill Road.doc | Approved | Pending | High | 0% | Rockdale-St. Lawrence 345 kV line Assorted 138 kV fixes | [5 empty] | As long as generation is available at Concord, risks associated with delaying this project are low. | ATC - Paul Hesse | Address unacceptably low voltages and overloads under system normal and single contingency conditions in Jefferson, Waukesha, and Washington counties. This project will improve west-east transfer capability within ATC footprint and reduce system losses significantly. Eliminate the need to run expensive Germantown and Concord generation units for voltage support. | [6 empty] | Y
345 | 2005-07-11 | newgrp20 | C-WUMS | ATC LLC | Morgan - Werner West 345 kV line (includes Clintonville-Werner West 138) | Morgan - Werner West 345 kV line, Clintonville - Werner West 138 kV line primarily on 345 kV line structures, and terminate the existing Werner - White Lake 138 kV line at the Werner West switching station | WI |  |  | The Morgan - Werner West 345kV line connects the radial 345kV line from Dead River - Plains - Morgan to the 345kV system in central Wisconsin. The Clintonville - Werner West 138kV line provides another outlet out of the new Werner West ss. Also strenghens the 138kV system in the area. |  | Approved | Pending | Low | 0% | 1. Morgan-North Appleton alternative Construct a new Morgan-N Appleton 345/138 kV double circuit line (assumed 42-mile length) 2. Low Voltage Enhancements alternative Add a 4th 345/138 kV transformer at N Appleton and construct a 138 kV ring bus. Rebuild various 138 kV lines. | [7 empty] | The transmission system from the Appleton area north to the Upper Peninsula of Michigan is the most constrained area on the ATC system. Numerous transmission lines and transformers are routinely operated near system security limits. To ensure that these security limits are not violated for various line outages, transmission service is routinely denied or interrupted and/or generation must be routinely redispatched. The cost of this generation redispatch has totaled about $2.1 million in 2001. This amount has increased from $2.1 million in 2001 to $5.9 in 2003. In addition, the reliability of transmission service to northeast Wisconsin and the Upper Peninsula of Michigan has proven to be inadequate, with three incidents in recent years in which partial or total blackouts have occurred. ATC has analyzed the widespread and chronic constraints and the blackouts and have evaluated various solutions for addressing these issues. One of the projects within ATC’s comprehensive plan involves a new 345 kV line, approximately 50 miles in length, from a planned new substation west of Appleton, currently referred to as Werner West, north to the existing Morgan substation. This project resolves numerous constraints in and around the Green Bay area, significantly improves reliability in northeast Wisconsin and the Upper Peninsula of Michigan, ties the 345 kV network in the northern-most part of ATC’s system to the southern portion of ATC’s system, enhances the performance of the other seven reinforcement projects, significantly reduces system losses and provides a strategic interconnection point for a planned outlet for the planned new Unit 4 generator at Weston. This project could be implemented without the significant number and duration of outages that would be required if each constraint was addressed individually. This project as proposed would also include a new 138 kV circuit from the Werner West substation to the Clintonville substation. This portion of the project would connect two 138 kV networks west of Green Bay and Appleton, mitigate constraints that would otherwise need to be addressed and enhance the value of the other reinforcements in ATC’s plan for this area. | [6 empty] | Y |  |  | Service
347 | 2005-07-11 | newgrp21 | C-WUMS | ATC LLC | Rubicon-Hustisford-Horicon 138 kV | Construct a Rubicon-Hustisford 138 kV line, Rebuild Hustisford-Horicon 69 kV to 138 kV, Construct 138/69 kV substation at a site near Horicon and install a 138/69 kV transformer | WI |  |  | The proposed project is needed to relieve several area 69 kV and 138 kV buses low voltages during several key contingencies. The Academy 138/69 kV transformer that supplies power into Beaver Dam and several 69 kV lines feeding the county will be susceptible to overloads under contingency as well. This project is therefore needed for the following reasons: 1. To support area voltages at Juneau, North Beaver Dam and Fox Lake substations under contingency. These voltages are projected to fall below secure operating conditions (as low as 88%) by 2008. 2. To offload the Academy 138/69 kV transformer under contingency. This transformer is projected to be loaded as high as 105% of its emergency rating by 2008. 3. To relieve the Academy to Columbus 69 kV line loading under contingency. This line is projected to be loaded as high as 102% of its emergency ratings by 2008. 4. To relieve the South Fond Du Lac to Springbrook 69 kV line loading under contingency This line is projected to be loaded as high as 99% of its 5. To relieve the North Beaver Dam to 3rd Street 69 kV line loading under contingency. This line is projected to be loaded as high as 99% of its emergency ratings by 2008. 6. To relieve low voltages at Oakfield and Mayville under contingency. 7. To provide for future system needs and expansion. | ATC Rubicon-Horicon.doc | Pending | Required | Low | 0% | Alternative 1: Conversion of Academy to South Beaver Dam line to 138 kV and New South Beaver Dam to Prospect Street Line Alternative 2: Rebuild and Conversion of South Fond Du Lac to Springbrook 69 kV line to to 138 kV | [14 empty] | Y |  |  | Share
352 | 2006-03-16 | newgrp4 | C-WUMS | ATC LLC | Cranberry-Conover 115 kV and Conover-Plains conversion to 138 kV | Construct Cranberry-Conover 115 kV line, Rebuild/convert Conover-Plains 69 kV line to 138 kV, Construct 138 kV bus and install 138/115 kV 150 MVA and 138/69 kV 60 MVA transformers at Conover, Construct 138 kV bus and install 60 MVA transformer at Bobcta, Relocate Iron River substation (Iron Grove), Construct 138 kV bus and install a 138/69 kV, 60 MVA transformer at Iron Grove | WI |  |  | This line connects the weak Rhinelander loop area with the Upper Peninsula of Michigan by converting a 69kV line to 138kV operation and extending it on new ROW to the Rhinelander area. The potential for overloads, low voltages, and even voltage collapse on the Rhinelander Loop and the Western Upper Peninsula of Michigan transmission systems have precipitated the need for immediate system reinforcements in these areas. |  | Approved | Pending | Low | 0% | Alternative #1: Weston - Venus 115 kV line and 115 kV line Rebuilds Alternative #2: Clear Lake - Park Falls 115 kV line Alternative #3: Venus - Plains 138 kV line | [5 empty] | No increased risk | ATC - Paul Hesse | [7 empty] | Y |  |  | Service
356 | 2006-03-16 | newgrp6 | C-WUMS | ATC LLC | Rockdale-West Middleton 345 kV | Construct 345 kV line from Rockdale to West Middleton, Construct a 345 kV bus and install a 345/138 kV 500 MVA transformer at West Middleton, Expand Rockdale 345 kV substation | WI |  |  | This project is needed to support area loads under several system outages in the southern and central Madison area. In particular, this new line provides support to prevent widespread voltage collapse in the Madison area for the loss of three Madison area 138 kV lines. | ATC Rockdale-West Middleton.doc | Pending | Pending | High | 0% | No other reasonable transmission alternatives exist, that is, numerous 138 kV facilities would need to be constructed in lieu of the preferred project. | [5 empty] | No increased risk | ATC - Paul Hesse | This project is needed to support area loads under several system outages in the southern and central Madison area. In particular, this new line provides support to prevent widespread voltage collapse in the Madison area for the loss of several 138 kV lines (North Madison-ABS 138 kV lines including North Madison-Huiskamp (proposed to be completed in 2008) and North Madison-West Middleton 138 kV line). | [6 empty] | Y |  |  | Share
432 | 2005-07-11 | 313 | C-WUMS | ATC LLC | Summit Lake Upgrade existing 11.3 to 16.9 MVAR capacitor bank | Summit Lake 115, install additional 5.6 Mvars of capacitance | WI |  |  | Antigo load serving problems are the main reason for upgrading the Summit Lake Cap Bank. Without additional reactive power support in that area, the bus voltages at the Antigo and Aurora St. substation for summer 2007 forecasted loads will drop below 0.9 p.u. under single contingency system conditions. Switching the 16.9 Mvar cap bank will cause 2.32% voltage change. This project will not only meet the near term needs of the Antigo area, but it will also remain useful when the Cranberry-Conover project is implemented in 2008. |  | Pending | Not Required |  | 0% | [15 empty] | Y |  |  | Excluded
433 | 2005-07-11 | 314 | C-WUMS | ATC LLC | Wautoma 32.6 MVAR capacitor bank | Install 2-24.5 MVAR capacitor banks at Wautoma 138 kV and one-16.33 MVAR capacitor bank at 69 Kv | WI |  |  | The 138 kV bus voltage at the Wautoma Substation is below ATC Planning criteria for system intact conditions in the 2006 summer peak TYA model. For N-1 conditions in the same summer model, Wautoma 138 kV bus voltages violate ATC Planning criteria. |  | Pending | Not Required |  | 0% | [15 empty] | Y |  |  | Excluded
434 | 2005-07-11 | 315 | C-WUMS | ATC LLC | Butternut 28.8 MVAR capacitor bank | Butternut 138, 28.8 MVAR Capacitor bank | WI |  |  | As shown in the 2004 TYA, impending low voltage problem (91 %) at Butternut 138 kV substation is expected in 2009 time frame during the outage of South Fond du Lac-Butternut 138 kV line. The proposed project will improve the voltage at Butternut under the critical contingency. |  |  |  | Low | 0% | [15 empty] | Y
446 | 2005-07-11 | 325 | C-WUMS | ATC LLC | Hartford 36 MVAR capacitor bank | Hartford 138 kV, 36 MVAR Capacitor bank | WI |  |  | Load growth in the Washington County area is leading to low voltages. |  | Approved | Not Required | [17 empty] | Y |  |  | Excluded
544 | 2005-07-11 | p2-104 | C-WUMS | ATC LLC | Bluemound 200 MVAR capacitor bank | Bluemound 200 MVAR capacitors | WI |  |  | Local 138 and 230kV system normal and contingent voltages in the Milwaukee metro area are sagging at time of system peak. Under various contingencies, the Bluemound 230kV bus voltage will drop to around 0.90 pu. | [20 empty] | Y |  |  | Not Shared
551 | 2005-07-11 | p2-110 | N-NM | ATC LLC | Stone Lake Substation | Stone Lake 345/161 tap of Arrowhead-Gardner Park 345 kV line | WI |  |  | A permanent Stone Lake 3451161 kV substation will provide several system benefits. The project will significantly reduce the reactive power requirements for the Arrowhead-Gardner Park 345 kV line. The project will increase the Arrowhead-Gardner Park 345 kV line power transfer capability. The project will allow the wheeling of additional power to the Xcel Energy transmission system. | ATC Appendix A update 092704.doc | Pending | Required |  | 0% | [9 empty] | 2004-09-30 | 2004-11-08 | Y | 2004-11-12 |  |  | Y |  |  | Excluded
566 | 2005-07-11 | 566 | C-WUMS | ATC LLC | Plymouth T-D interconnection | Forest Junction / Charter Steel to Plymouth 138 kV line and T-D substation. Construct 1.3 mile double circuit from Plymouth municipal utility to existing line. | WI |  |  | New load by a major industrial customer at Plymouth requires an additional substation to alleviate low voltage conditions during normal service and to cover first contingency alternate feeds for outages to 12.47 kV feeders and the loss of Plymouth 773 substation. | ATC Appendix A update 092704.doc | not budgeted | Not Required | Low | 0% | [9 empty] | 2004-09-30 | 2004-11-08 | Y | 2004-11-12 |  |  | Y |  |  | Excluded
567 | 2005-07-11 | 567 | C-WUMS | ATC LLC | North Appleton-Lawn Road-White Clay 138 kV uprate | North Appleton - Lawn Road - White Clay 138 kV line upgrade. This project increases line clearance on the 30 mile line. | WI |  |  | When replacement of the terminal equipment at the White Clay and North Appleton 138 kV substations is complete, the most limiting facility of line KK6851 becomes the line conductor (795 ACSR 26/7,29.8 miles) at normal and emergency conductor temperatures of 167 degrees F. Increasing the line clearance to achieve normal and emergency conductor temperatures of 200 degrees F will allow increased Flow South (Wisconsin-Michigan) capability when the Morgan-White Clay 138 kV line reconductoring project is complete. | ATC Appendix A update 092704.doc | not budgeted | Not Required | Low | 0% | [9 empty] | 2004-09-30 | 2004-11-08 | Y | 2005-06-16 |  |  | Y |  |  | Excluded
568 | 2005-07-11 | 568 | C-WUMS | ATC LLC | North Lake Geneva - White River 138 kV line | North Lake Geneva - White River 138 kV line | WI |  |  |  | ATC Appendix A update 092704.doc | Pending | Pending |  | 0% | [9 empty] | 2004-09-30 | 2004-11-08 | Y | 2004-11-12 |  | ??? | Y |  |  | Excluded
569 | 2005-07-11 | 569 | C-WUMS | ATC LLC | White River T-D interconnection | South Lake Geneva - White River 138 kV line | WI |  |  | Present distribution system faces low voltages and overloads under contingency. The substation transformers and feeders in the area cannot support the present load and are in need of additional support for the anticipaed load growth in the area. | ATC Appendix A update 092704.doc | [19 empty] | Y |  |  | Not Shared
570 | 2005-07-11 | 570 | C-WUMS | ATC LLC | Rock River-Bristol-Elkhorn conversion to 138 kV | Rock River - Bristol - Elkhorn conversion to 138 kV | WI |  |  | Present transmission system faces several serious low voltages (as low as 0.86p.u.) and overloads (as high as 136% over emergency rating) under single contingency. Two 69 kV lines that are in parallel with one 138 kV line feeding the eastern Rock and Walworth county are overburdened due to higher than average load growth in Walworth county. Transmission system reinforcements are needed to reliably serve loads in the area. An Operating Guide is presently being used to prevent severe overloads on Y32 (Colley Road to Brick Church 69 kV) line under contingency. Continuing use of this guide for an extended period of time is not desirable. | ATC Appendix A update 092704.doc | Pending | Pending | High | 0% | [6 empty] | Project under review |  |  | 2004-09-30 | 2004-11-08 | Y | 2004-11-12 |  |  | Y |  |  | Excluded
571 | 2005-07-11 | 571 | C-WUMS | ATC LLC | North Madison-Waunakee 138 kV line | New North Madison - Huiskamp 138 kV line and a new 138/69 kV substation near Huiskamp including a 100 MVA 138/69-kV transformer | WI |  |  | This project is needed to support area loads under several system outages in the northern and central Madison area. | ATC Appendix A update 092704.doc | Pending | Pending | [11 empty] | 2004-09-30 | 2004-11-08 | Y | 2004-11-12 |  |  | Y |  |  | Excluded
572 | 2005-07-11 | 572 | C-WUMS | ATC LLC | Menominee 138/69 kV transformer | Loop West Marinette - Bay de Noc 138 kV line into Menominee. Total project cost $2,000,000. | WI |  |  | The proposed project is needed to address the impending and potential overloads expected in 2009 shoulder peak time periods. Roosevelt 138169 kV transformer would be loaded at 96.3 % under the contingency of West Marinette-Wells St 69 kV or West Marinette 138169 kV transformer #1 or #2. The West Marinette #1 or #2 would loaded at 102% -105% under the contingency of Wells St-Roosevelt Rd 69 kV line or Roosevelt Rd 13 8/69 kV transformer. | ATC Appendix A update 092704.doc | not budgeted | Not Required | Low | 0% | [9 empty] | 2004-09-30 | 2004-11-08 | Y | 2004-11-15 |  |  | Y |  |  | Excluded
573 | 2006-07-05 | 573 | C-WUMS | ATC LLC | North Madison-West Middleton 345 kV | North Madison - West Middleton 345 kV line | WI |  |  | This project is needed to support area load under several system outages in the southern and central Madison area. In particular, this new line provides support to prevent widespread voltage collapse in the Madison area for the loss of the Rockdale to West Middleton 345 kV line. This line will complete 345 kV loop around Madison. | ATC Appendix A update 092704.doc |  | Required | [9 empty] | ATC - Wenchun Zhu |  |  |  |  | 2005-06-16 |  |  | Y
574 | 2005-07-11 | 574 | C-WUMS | ATC LLC | Monroe County - Council Creek 161 kV line projects | Monroe County - Council Creek 161 kV line, Council Creek 161/138 kV transformer; Petenwell-Saratoga 138 kV rebuild and Council Creek-Petenwell uprate 138 kV | WI |  |  | Reliability in the Tomah area. Tomah area voltage for bus-tie outage and next outage will be below 90%. The solution improves voltages as far away as Petenwel, Hilltop, and Kilbourn. | ATC Appendix A update 092704.doc | Pending | Required |  | 0% | [15 empty] | Y |  |  | Share
575 | 2006-03-16 | 575 | C-WUMS | ATC LLC | Pulliam-New Suamico conversion to 138 kV for T-D interconnection | Rebuild/Convert Pulliam-New Suamico 69 kV line to 138 kV | WI |  |  | The new Suamico T-D interconnection (2007) would require a new substation due to the limitation to the size of the existing substation. Additionally, the towers on Line T-98 (Pulliam-Suamico-Sobieski) date back to 1911, and the lines with 110 copper hemp center remaining conductor life is estimated to be zero year. The proposed project will address these issues and provide a valuable opportunity for operational / maintenance flexibility and network service to the Bayport and the new Suamico substations via a future 138 kV line from the new Suamico substation to the existing Pioneer substation. | ATC Pulliam-New Suamico.doc | Pending | Pending | Low | 0% | 1) Rebuild Pulliam-New Suamico 69 kV line using various conductor sizes 2) Rebuild/convert Pulliam-New Suamico 69 kV line to double circuit 138 kV | [5 empty] | This project is driven primarily by load serving issues. It will also provide better reliability under multiple contingency condition and address the line condition issue. | ATC - Paul Hesse | [7 empty] | Y |  |  | Share
682 | 2006-02-17 |  | C-WUMS | ATC LLC | Huiskamp-Blount 138 kV line | Convert Huiskamp-Blount 69 kV line to 138 kV | WI |  |  | This project is needed to support area loads under several system outages in the northern and central Madison area. In particular, the new line provides support to prevent widespread voltage collapse in the Madison area for the outage of North Madison-Sycamore 138 kV line. |  | Pending | Pending | Low | 0% | a) Sycamore-Ruskin 69 kV circuit b) Yahara River-Waunakee 69 kV circuit | [14 empty] | Y |  |  | Share
877 | 2006-03-16 | new100 | C-WUMS | ATC LLC | Elm Road (Oak Creek) Generation Related Additions | Reconductor Oak Creek-Ramsey 138 kV line (2009), Reconductor Oak Creek-Allerton 138 kV line (2009), Replace relaying on 230 kV circuits at Oak Creek (2009), Replace two 345 kV circuit breakers at Pleasant Prairie on the Racine and Zion lines with IPO breakers and upgrade relaying (2009), Expand Oak Creek 345 kV switchyard to interconnect one new generator (2009), Loop Ramsey5-Harbor 138 kV line into Norwich and Kansas to form a new line from Ramsey-Norwich and Harbor-Kansas 138 kV lines (2009), Uprate Kansas-Ramsey6 138 kV line (2009), Install second 500 MVA 345/138 kV transformer at Oak Creek (2010), Expand 345 kV switchyard at Oak Creek to interconnect one new generator (2010), Uprate Oak Creek-Root River 138 kV line (2010), Uprate Oak Creek-Nicholson 138 kV line (2010), Expand Oak Creek 345 kV switchyard to interconnection three new generators plus one new 345 kV line and 138 kV switchyard to accommodate new St. Martins line (2013), Construct a 345/138 kV switchyard at Hale (Brookdale) to accommodate two 345 kV lines, a 500 MVA 345/138 kV transformer and 4-138 kV lines plus two 138-26.2 kV transformers (2013), Install two 345 kV line terminations at Pleasant Prairie and loop Zion-Arcadian 345 kV line into Pleasant Prairie substation (2013), Construct an Oak Creek-Hale (Brookdale) 345 kV line installing 4 mi. new structures, converting 16.2 mi. of non-operative 230 kV and 5 mi. 138 kV (2013), Construct Oak Creek-St Martins 138 kV circuit #2 installing 16.6 mi. conductor on existing towers (2013), Construct a Hale (Brookdale)-Granville 345 kV line converting/reconductoring 5.6 mi. 138 kV, rebuilding 7 mi. 138 kV double circuit tower line and converting/reconductoring 3 mi. 138 kV on existing 345 kV structures (2013), Restring Bluemound-Butler 138 kV line (KK5051) on new 345 kV structures installed with Hale (Brookdale)-Granville line (2010), String Butler-Tamarack (Carmen) 138 kV line on new 345 kV structures installed with Hale (Brookdale)-Granville line (2013), Replace CTs at Racine 345 kV substation (2013) | WI |  |  | To accommodate 1950 MW of additional generation at the Elm Road (Oak Creek) site. Generator-Transmission interconnection G051 | ATC Elm Road Generation Additions.doc | Approved | Pending | High | 0% | There were no viable alternatives considered for this project. The projects listed above made use of existing rights-of-way and upgrading existing facilities to accommodate the new generation. | [5 empty] | Once additional generation (2009) is placed in service at Oak Creek, the existing 345/138kV xfmr will overload under contingency. | ATC - Paul Hesse |  | 2005-07-11 | [5 empty] | Y |  |  | Service
880 | 2005-07-11 | new103 | C-WUMS | ATC LLC | Lost Dauphin-North Appleton-Mason Street 138 kV uprates | Lost Dauphin-North Appleton-Mason Street 138 kV uprates | WI |  |  | Transmission service request 75796129 | [14 empty] | 2005-07-11 | [5 empty] | Y |  |  | Service
882 | 2006-07-05 | new105 | C-WUMS | ATC LLC | Octonagon 16.32 MVAR capacitor bank | Octonagon 16.32 MVAR capacitor bank | MI |  |  | Local 138 and 69 kV system normal and contingent voltages in the northwestern Upper Peninsula of Michigan continue to be a concern. Voltages in the area could drop as low 89% of their nominal voltage for the loss of the Perch Lake-M38 138 kV line under 2006 summer peak conditions and as low as 74% under the 2010 summer peak conditions as based on the latest UPPCO load forecasts which have been included in the 2005 Ten Year Assessment. The proposed capacitor installation would help to mitigate the current voltage concerns for an outage of the Perch Lake -M38 138 kV line. The capacitor installation would help mitigate low voltages in the area for eleven different potential contingencies. |  | Approved | Not Required | Low | 5% | [7 empty] | ATC - Wenchun Zhu |  | 2005-07-11 | [5 empty] | Y |  |  | Not Shared
884 | 2005-07-11 | new107 | C-WUMS | ATC LLC | Spring Green 32 MVAR capacitor bank | Spring Green 32 MVAR capacitor bank | WI |  |  | The 138 kV bus voltages at Spring Green, Troy, Eden and Kirkwood substations are at or below the minimum ATC Planning criteria for in tact system conditions in the 2014 summer peak TYA model. This clearly demonstrates a need for reactive power support in the area. | [14 empty] | 2005-07-11 | [5 empty] | Y |  |  | Not Shared
886 | 2005-07-11 | new109 | C-WUMS | ATC LLC | North Lake (Cedar) sub relocation | North Lake (Cedar) substation relocation | MI |  |  | Age, condition, and maintenance requirements of the Cedar Substation; improved reliability in the north central Upper Peninsula. | MTEP06 Large Project Reporting Form - North Lake (Cedar) Substation Relocation.doc | Approved | N/A | High | 0% | Rebuild existing Cedar substation in present location. | [5 empty] | Cedar substation renamed to North Lake |  |  | 2005-07-11 | [5 empty] | Y |  |  | Share
887 | 2005-07-11 | new110 | C-WUMS | ATC LLC | Bain 345 kV bus | Bain 345 kV bus | WI |  |  | Opening bus-tie breaker 34 at Pleasant Prairie results in Pleasant Prairie generator #2 being isolated on Bain transformer #5. The transformer has a short term rating of about 560 MVA and a long-term SELD rating of 453MVA. The generator is capable of more than 600 MW output. With the bus tie breaker open or out of service, Pleasant Prairie generator #1 must be backed down under contingency. The Bain 345kV bus is one long-term solution that is being considered. | [14 empty] | 2005-07-11 | [5 empty] | Y |  |  | Not Shared
888 | 2005-07-11 | new111 | C-WUMS | ATC LLC | Plains second 345/138 kV transformer | Plains second 345/138 kV transformer | MI |  |  | As the Northern Umbrella Plan projects are completed, the import level to the Upper Peninsula will be greater than 350 MVA. At these levels single contingency outages result in overload of the existing 345-138 kV transformer. | [14 empty] | 2005-07-11 | [5 empty] | Y |  |  | Share
889 | 2005-07-11 | new112 | C-WUMS | ATC LLC | Brule substation relocation | Brule (renamed Aspen) substation relocation | MI |  |  | This project is needed due to the age, condition, and maintenance requirements of the Brule Substation; improved reliability in the Upper Peninsula. | MTEP06 Large Project Reporting Form Brule (Bobcat) Relocation.doc | Approved | Pending | Low | 0% | No viable alternatives are available for this project. | [5 empty] | Brule will become Aspen |  |  | 2005-07-11 | [5 empty] | Y
1256 | 2006-05-08 | 1256 | C-WUMS | ATC LLC | Paddock - Rockdale 345kV | Paddock - Rockdale 345kV circuit #2 and supporting projects of lower voltage levels | WI |  |  | ATC Access project. Customer, stakeholder and the PSCW feedback led ATC's 2005 Access Initiative to the conclusion that the 2nd Paddock - Rockdale 345 kV circuit (along with some related supporting projects) provide economic congestion relief benefits that exceed the construction cost of the project. |  | Proposed | Required | Low | 0% | [7 empty] | Wenchun Zhu |  | 2006-05-08 | [5 empty] | Y
1267 | 2006-07-05 | new1 | C-WUMS | ATC LLC | New Oak Ridge-Verona 138-kV line and a 138/69-kV transformer at Verona | Construct new Oak Ridge-Verona 138-kV line and install a 138/69-kV transformer at Verona | WI | [15 empty] | ATC - Wenchun Zhu |  | 2006-07-05 | [5 empty] | Y
1268 | 2006-07-05 | new2 | C-WUMS | ATC LLC | Cap banks at Artesian and Kilbourn | Install 2-16.33 MVAR 69 kV capacitor banks at Kilbourn and install 2-24.5 MVAR 138-kV capacitor banks at Artesian | WI | [15 empty] | ATC - Wenchun Zhu |  | 2006-07-05 | [5 empty] | Y
1269 | 2006-07-05 | new3 | C-WUMS | ATC LLC | Arcadian transformer replacement | Replace Arcadian 345/138kV transformer #3 with a 500MVA transformer. | WI |  |  |  |  | Proposed | not required | High | [8 empty] | ATC - Wenchun Zhu |  | 2006-07-05 | [5 empty] | Y
1270 | 2006-07-05 | new4 | C-WUMS | ATC LLC | Upgrade Arcadian - Waukesha 138kV lines | Increase clearances of the two Arcadian - Waukesha 138kV lines | WI |  |  |  |  | Not Budgeted | Not Required | High | [8 empty] | ATC - Wenchun Zhu |  | 2006-07-05 | [5 empty] | Y
1271 | 2006-07-05 | new5 | C-WUMS | ATC LLC | Upgrade Oak Creek - Pennsylvania 138kV line | Increase clearance of the Oak Creek - Pennsylvania 138kV line | WI |  |  |  |  | Not Budgeted | Not Required | High | [8 empty] | ATC - Wenchun Zhu |  | 2006-07-05 | [5 empty] | Y
42 | 2005-07-11 | 17 | E-MIO | CIN | Bedford to Seymour 13829 Reconductor | Reconductor 13829 line from Bedford - Shawswick - Pleasant Grove - Airport Road Jct - Seymour. | IN |  |  | Line overloads for loss of Bedford to Columbus 345kV line. |  | Approved | Not Required | Medium | 0% | [15 empty] | Y |  |  | Excluded
91 | 2005-07-11 | 72 | E-MIO | CIN | Hillcrest 345/138 | Construct new 345/138 kV Hillcrest substation. Tap Suart to Foster 345kV line. Construct new 138kV line from Eastwood to Hillcrest. | OH |  |  | Delay of this project will cause the Stuart 345/138kV transformer to exceed its normal rating and exceed its emergency rating during an outage. Line 5484 will exceed the low voltage limit for an outage. Brown TB1 and Eastwood TB2 will exceed their ratings. |  | Approved | Not Required | Medium | 0% | [15 empty] | Y |  |  | Share
115 | 2005-07-11 | 86 | E-MIO | CIN | New London to Webster 230 Reconductor | Reconductor New London to Webster St 230 | IN |  |  | The New London to Webster St. 230 kV circuit will overload for loss of the AEP Jefferson to Greentown 765 kV circuit under high transfer conditions --specifically south to north and west to east. It consistently shows up as a limit under various transfer scenarios in the ECAR summer seasonal and future system assessments. Based on actual 2003 loadings, this circuit would have exceeded its contingency loading twenty- three hours in 2003. There is an existing operating procedure that is used to reduce loading on this circuit that involves splitting the 138 kV bus at Greentown and opening the 230 kV circuit from Noblesville to Kokomo. As the load in the Kokomo area increases and high transfer levels continue to exist, this operating procedure will no longer be effective in relieving the contingency overload. |  | Approved | Not Required | Medium | 0% | [15 empty] | Y |  |  | Excluded
116 | 2005-07-11 | 87 | E-MIO | CIN | Westwood Bk2 345/138 | Add 2nd 345kV line from AEP Dequine to Westwood and 2nd Westwood 345/138 kV transformer. | IN |  |  | These projects are the preferred plan resulting from a 2003 T&D Planning 10 year study of the Lafayette 138 KV system. Starting in 2007, the loss of the Westwood transformer causes two criteria violations - low voltage on the Lafayette 230 KV bus and overloading of Lafayette Bank 1. This project also facilitates load shifting from the 230kv system to the 345kv system to reduce loading and improve voltage on the 230kv system in northern Indiana. |  | Approved | Not Required | Medium | 0% | [15 empty] | Y |  |  | Excluded
199 | 2005-07-11 | 178 | E-MIO | CIN | Kokomo HP 230/138 | Add 4th 230/138 kV transformer at Kokomo Highland Park. | IN |  |  | The Kokomo Highland park 230-138 kV transformers will overload for loss of the AEP Jefferson to Greentown 765 kV circuit (NERC Category B event) under conditions of high transfers across the Cinergy system -- specifically south to north and west to east. These banks consistently show up as a limit under various transfer scenarios in the ECAR summer seasonal and future system assessments. |  | Approved | Not Required | Medium | 0% | [15 empty] | Y |  |  | Excluded
200 | 2005-07-11 | 179 | E-MIO | CIN | W Laf Purdue 138 Switches | Upgrade 138kV switches at West Lafayette Purdue. | IN |  |  | Switches are overloaded under contingency conditions. |  | Approved | Not Required | Medium | 0% | [15 empty] | Y |  |  | Excluded
201 | 2005-07-11 | 180 | E-MIO | CIN | W Laf 138 Switches | Changing out switches to achieve conductor rating. NW Tap - West Lafayette 138 | IN |  |  | Switches are overloaded under contingency conditions. |  | Approved | Not Required | Medium | 0% | [12 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
618 | 2005-07-11 |  | E-MIO | CIN | Beckjord 138 Reconfigure | Rebuild the Beckjord 138 Substation so it can be tied together under normal conditions. | OH |  |  | Under certain conditions such as high transfers, various generation dispatch scenarios and/or contingencies the 138 circuits from Beckjord reach their emergency ratings. |  | Approved | Not Required | Medium | 0% | [15 empty] | Y |  |  | Excluded
619 | 2006-03-10 |  | E-MIO | CIN | IPL Petersburg 345 Breaker | Complete breaker and half scheme at Petersburg Plant. IPL total estimate 1,100,000. 200,000 is Cinergy share of project. | IN |  |  |  |  | Approved | Not Required | High | 0% | [6 empty] | Project funding is currently under evaluation by IPL with an in-service date of 12/31/06 at the earliest due to construction scheduling restrictions caused by the Pete-Hanna 345 tornado damage. Cinergy and Vectren have agreed to fund the project. | CIN - Jim Doell |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
624 | 2005-07-11 |  | E-MIO | CIN | Cloverdale to Plainfield 138 Lightning Protection | Upgrade static and grounding on the Cloverdale to Plainfield South 138kV circuit. | IN |  |  | This was a project to increase the reliability for this line. Project changed from reconductor to upgrading static and grounding only. |  | Approved | Not Required | Medium | 0% | [12 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
625 | 2006-07-05 |  | E-MIO | CIN | Pierce/Beckjord 345/138 kV transformer addition | Add 3rd 345/138kV transformer, 400MVA, from Pierce 345kV bus to Beckjord 138kV North bus. | OH |  |  |  |  | Budgeted | Not Required | [17 empty] | Y |  |  | Excluded
627 | 2005-07-13 | 304D7834 | E-MIO | CIN | Kenton to West End New 138 Circuit | Construct new 138kV line from Kenton to West End. | KY | OH |  | Exceed thermal overload on several 138kV lines. |  | Approved | Obtained | Medium | 0% | [12 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
628 | 2005-07-11 |  | E-MIO | CIN | Kok HP to Kok Delco 138 100C Uprate | Uprate 138kV line from Kokomo Highland Park to Kokomo Delco to 100C operating temperature. | IN |  |  | This line is a main feed through from Kokomo Highland Park substation to Greentown under 765kV outage conditions and could overload for high South to North transfer scenarios especially as transformer capacity is increased at Highland Park. |  | Approved | Not Required | Medium | 0% | [15 empty] | Y |  |  | Excluded
629 | 2005-07-11 | 628A | E-MIO | CIN | Kok HP to Kok Chrysler 138 100C Uprate | Uprate 138kV line from Kokomo Highland Park to Kokomo Chrysler to 100C operating temperature. | IN |  |  | This line is a main feed through from Kokomo Highland Park substation to Greentown under 765kV outage conditions and could overload for high South to North transfer scenarios especially as transformer capacity is increased at Highland Park. |  | Approved | Not Required | Medium | 0% | [15 empty] | Y |  |  | Excluded
631 | 2005-07-11 |  | E-MIO | CIN | Columbus 600A 138kV Switches | Replace 600A switches at Columbus. Increase rating for Columbus to Seymour 13830 circuit. | IN |  |  | The 2009 model indicates that for an outage of the Bedford to Shawswick 138kV line the Bedford to Seymour 138kV line overloads. The 600A switches at Columbus are limiting the line to a 143 MVA rating. Replacing these switches will result in a rating increase to 179 MVA. |  | Approved | Not Required | Medium | 0% | [15 empty] | Y |  |  | Excluded
632 | 2005-07-11 |  | E-MIO | CIN | Gallagher to HE Georgetown 138kV Reconductor | Reconductor section of the 13885 circuit from Gallagher to HE Georgetown. | IN |  |  | The loss of the Edwardsport to Whitfield 13824 line causes the Gallagher to HE Georgetown 13885 circuit to overload. |  | Approved | Not Required | Medium | 0% | [15 empty] | Y |  |  | Excluded
765 | 2005-07-11 |  | E-MIO | CIN | Cloverdale 138kV Cap | Add 43.2 MVAR 138kV capacitor at Cloverdale. | IN |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not Required | Medium | 0% | [12 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
766 | 2005-07-11 |  | E-MIO | CIN | Clarksville 138kV Cap | Add 57.6 MVAR 138kV capacitor at Clarksville. | IN |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not Required | Medium | 0% | [15 empty] | Y |  |  | Excluded
767 | 2005-07-11 |  | E-MIO | CIN | Hastings Park 138kV Cap | Add 57.6 MVAR 138kV capacitor at Greenfield Hastings Park. | IN |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not Required | Medium | 0% | [15 empty] | Y |  |  | Excluded
795 | 2005-07-11 |  | E-MIO | CIN | Geist 69kV Cap | Add 35 MVAR 69kV capacitor at Geist. | IN |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not required | Medium | 0% | [15 empty] | Y
806 | 2005-07-11 | A | E-MIO | CIN | Gwynnville 345/69 | Add 345/69kV transformer at Gwynnville. Construct four 69kV exits to connect to existing 69kV circuits. | IN |  |  | Add 69kV capacity. |  | Approved | Not required | Medium | 0% | [15 empty] | Y
807 | 2005-07-11 | B | E-MIO | CIN | Dresser Bk 1&2 Limiting Equipment | Replace 138kV breakers and switches to achieve full transformer rating. | IN |  |  | Loss of one transformer at Dresser will overload the remaining transformer. |  | Approved | Not required | Medium | 0% | [15 empty] | Y |  |  | Not Shared
810 | 2005-07-11 | E | E-MIO | CIN | Bloomington Bk3 230/69 | Add 2nd 230/69kV transformer at Bloomington. | IN |  |  | Add 69kV capacity. |  | Approved | Not required | Medium | 0% | [15 empty] | Y
811 | 2005-07-11 | F | E-MIO | CIN | Evendale 69kV Caps 1&2 | Add two 21.6 MVAR 69kV capacitors at Evendale | OH |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not required | Medium | 0% | [15 empty] | Y
819 | 2005-07-11 | N | E-MIO | CIN | Bedford 69kV Cap | Add 50.4 MVAR 69kV capacitor at Bedford. | IN |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not required | Medium | 0% | [15 empty] | Y
820 | 2005-07-11 | O | E-MIO | CIN | Loogootee 69kV Cap | Add 7.2 MVAR 69kV capacitor at Loogootee. | IN |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not required | Medium | 0% | [15 empty] | Y
821 | 2005-07-11 | P | E-MIO | CIN | Orleans South 69kV Cap | Add 14.4 MVAR 69kV capacitor at Orleans South. | IN |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not required | Medium | 0% | [15 empty] | Y
823 | 2005-07-11 | R | E-MIO | CIN | Terminal 69kV Cap | Add 28.8 MVAR 69kV capacitor at Terminal. | OH |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not required | Medium | 0% | [15 empty] | Y
824 | 2005-07-11 | S | E-MIO | CIN | Wilder 69kV Caps 1&2 | Add two 28.8 MVAR 69kV capacitors at Wilder. | KY |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not required | Medium | 0% | [15 empty] | Y
825 | 2005-07-11 | T | E-MIO | CIN | Wabash 69kV Cap | Add 28.8 MVAR 69kV capacitor at Wabash. | IN |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not required | Medium | 0% | [15 empty] | Y
826 | 2005-07-11 | U | E-MIO | CIN | Webster St 69kV Cap | Add 28.8 MVAR 69kV capacitor at Kokomo Webster St. | IN |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not required | Medium | 0% | [15 empty] | Y
828 | 2005-07-11 | W | E-MIO | CIN | Northgreen 69kV Cap | Add 14.4 MVAR 69kV capacitor at Northgreen. | OH |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not required | Medium | 0% | [15 empty] | Y
830 | 2005-07-11 | Y | E-MIO | CIN | Thorntown 69kV Cap | Add 28.8 MVAR 69kV capacitor at Thorntown. | IN |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not required | Medium | 0% | [15 empty] | Y
831 | 2005-07-11 | Z | E-MIO | CIN | Greensburg 69kV Cap | Add 28.8 MVAR 69kV capacitor at Greensburg. | IN |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not required | Medium | 0% | [15 empty] | Y
832 | 2005-07-11 | AA | E-MIO | CIN | Lebanon 69kV Cap | Add 21.6 MVAR 69kV capacitor at Lebanon. | IN |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not required | Medium | 0% | [15 empty] | Y
833 | 2005-07-11 | AB | E-MIO | CIN | Rochester 69kV Cap 2 | Add 2nd 21.6 MVAR 69kV capacitor at Rochester. | IN |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not required | Medium | 0% | [15 empty] | Y
834 | 2005-07-11 | AC | E-MIO | CIN | Kingman 69kV Cap | Add 7.2 MVAR 69kV capacitor at Kingman. | IN |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not required | Medium | 0% | [15 empty] | Y
835 | 2005-07-11 | AD | E-MIO | CIN | Pittsboro 69kV Cap | Add 14.4 MVAR 69kV capacitor at Pittsboro. | IN |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not required | Medium | 0% | [15 empty] | Y
836 | 2005-07-11 | AE | E-MIO | CIN | Inland Container 69kV Cap | Add 21.6 MVAR 69kV capacitor at Inland Container. | IN |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not required | Medium | 0% | [15 empty] | Y
837 | 2005-07-11 | AF | E-MIO | CIN | New Albany 69kV Cap | Add 28.8 MVAR 69kV capacitor at New Albany. | IN |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not required | Medium | 0% | [15 empty] | Y
838 | 2005-07-11 | AG | E-MIO | CIN | Speed 69kV Cap | Add 57.6 MVAR 69kV capacitor at Speed. | IN |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not required | Medium | 0% | [15 empty] | Y |  |  | Not Shared
839 | 2005-07-11 | AH | E-MIO | CIN | Crawfordsville 69kV Cap | Add 28.8 MVAR 69kV capacitor at Crawfordsville. | IN |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not required | Medium | 0% | [15 empty] | Y |  |  | Not Shared
840 | 2005-07-11 | AI | E-MIO | CIN | Rushville 69kV Cap | Add 14.4 MVAR 69kV capacitor at Rushville. | IN |  |  | Increase system reactive power resources and provide voltage support. |  | Approved | Not required | Medium | 0% | [15 empty] | Y
841 | 2005-07-11 | AJ | E-MIO | CIN | Westwood Bk1 Limiting Equipment | Replace 1200A 138kV equipment with 2000A to allow full transformer rating. | IN |  |  | The loss of Westwood Bk2 will cause the limiting equipment on Westwood Bk1 to overload. |  | Approved | Not required | Medium | 0% | [15 empty] | Y
842 | 2005-07-11 |  | E-MIO | CIN | Blackwell 138/69 | Construct new Blackwell 138/69kV substation. Tap LGEE 138kV line into substation. | KY |  |  | Add 69kV capacity. |  | Approved | Not required | Medium | 0% | [15 empty] | Y |  |  | Not Shared
844 | 2005-07-13 | AM | E-MIO | CIN | Newton 138/69 | Add new 138/69 kV TB at exsiting Newtown substation | OH |  |  | 69kV capacity needed to allow all load to be served for the loss of Oakley TB 1, Oakley TB 2, Summerside TB 2 or Tobasco TB 5. |  | Approved | Pending | Medium | 0% | [15 empty] | Y
845 | 2005-07-11 | AN | E-MIO | CIN | Stillwell 138/69 | Construct new Stillwell 138/69 kV substation in the area served by Fairfield and Collinsville | OH |  |  | 69kV capacity needed to allow all load to be served for the loss of Fairfield TB 2 or Collinsville TB 1, or loss of F9062 between Collinsville and McGuffey |  | Approved | Not required | Medium | 0% | [15 empty] | Y
847 | 2005-07-11 | AP | E-MIO | CIN | Gallagher RAT 11 | Install 138/4kV RAT 11and relocate the 138kV transfer breaker at Gallagher Gen Sta. | IN |  |  | Provide capacity for new pollution control equipment (bag house). |  | Approved | Not required | Medium | 0% | [15 empty] | Y
849 | 2005-07-11 | AR | E-MIO | CIN | Peabody Jct 600A Switches | Replace Peabody Jct 600A switches with 1200A switches. | IN |  |  | Replace obsolete and unreliable equipment. |  | Approved | Not required | Medium | 0% | [15 empty] | Y |  |  | Not Shared
850 | 2005-07-11 | AS | E-MIO | CIN | Northside to CMC 138 | Construct 138kV line from LGEE Northside to Clark Maritime Center. | IN |  |  | The Clark Maritime Center is an industrial park in Jeffersonville, IN which is served from a two mile 138kV radial tap line. The load served from the substation in this industrial park has grown to over 20 Mw. In the next five years the load could grow to over 50 Mw which would be at risk of a single 138kV line outage. The purpose of this project is to construct an alternate feed into this industrial park. |  | Approved | Not required | Medium | 0% | [15 empty] | Y |  |  | Not Shared
851 | 2005-07-11 | AT | E-MIO | CIN | Laf Cumberland to Laf AE Staley 138 Reconductor | Reconductor section of 13806 circuit with 954ACSR 100C. | IN |  |  | Cinergy studies indicate an outage of the 13808 line from Westwood to Lilly will cause this section to overload. |  | Approved | Not required | Medium | 0% | [15 empty] | Y |  |  | Not Shared
852 | 2006-07-05 | AU | E-MIO | CIN | Crawfordsville to Tipmont Concord to Lafayette SE 138 Reconductor | Reconductor 13819 circuit with 954ACSR 100C. | IN |  |  | Cinergy studies indicate an outageof the AEP 345 KV line from Dequine to Eugene causes this section to overload. A 13846 line outage between Rockville and Parke Co. REMC Marshall also causes the overload. New Ethanol plant load also being added to this line. |  | Approved | Not required | Medium | 0% | [15 empty] | Y |  |  | Not Shared
853 | 2005-07-11 | AV | E-MIO | CIN | West Lafayette to Cumberland 138 Reconductor | Reconductor section of 13806 circuit with 954ACSR 100C. | IN |  |  | The contingency projected to cause this line section overload is a 13808 line outage from Westwood to Lilly. |  | Approved | Not required | Medium | 0% | [15 empty] | Y
1193 | 2005-11-28 | 104F8436 | E-MIO | CIN | Nickel | Extend 5680 through new Nickel 138/12 sub to be built on development property. |  |  |  | Provide additional 12kV capacity. | [14 empty] | 2005-11-28 | [5 empty] | Y |  |  | Not Shared
1194 | 2005-11-28 | X02P6411 | E-MIO | CIN | Prescott | Add 43.2 MVAR capacitor. | IN |  |  | Increase system reactive power resources and provide voltage support. | [14 empty] | 2005-11-28 | [5 empty] | Y
1195 | 2005-11-28 | 604E6256 | E-MIO | CIN | Cloverdale Ethanol 138 | Construct new 138kV line from Cloverdale to new Putnam Energy ethanol plant. | IN |  |  | New line needed to serve new customer. | [14 empty] | 2005-11-28 | [5 empty] | Y |  |  | Not Shared
1196 | 2005-11-28 | 602F6290 | E-MIO | CIN | New London to Kok Highland Park 23009 Wave Traps | Replace 23009 800A wave traps at New London and Kokomo Highland Park with 1200A wave traps. | IN |  |  | Additional capacity is needed during construction of the new 230/138 xfr at Kok HP and the New London to Webster reconductor. | [14 empty] | 2005-11-28 | [5 empty] | Y |  |  | Not Shared
1197 | 2005-11-28 | X03C7992 | E-MIO | CIN | Evendale 138/34 | Replace failed transformer as two winding. New transf. To be connected to 138kV bus 2. | [18 empty] | 2005-11-28 | [5 empty] | Y
1198 | 2005-11-28 | 802F6503 | E-MIO | CIN | Bedford Switch Automation | Add motors and automation to the 34506 and 34521 line switches. | IN |  |  | Automating these switches will eliminate the tripping of Bedford 345/138 Bks 5 & 7 for faults on the 34506 and 34521 line. | [14 empty] | 2005-11-28 | [5 empty] | Y |  |  | Not Shared
1199 | 2005-11-28 | 804F6505 | E-MIO | CIN | Dresser to Water St 100C Urate | Uprate 13868 conductor to 100C operating temperature from Dresser to S 1st St to Water St. New limit 1200A terminal equipment. | IN |  |  | he Dresser to South 1st St to Water St 13868 line will overload for the loss of the Cayuga to Cayuga CT 345kV line or the Cayuga CT to Sugar Creek 345kV line. | [14 empty] | 2005-11-28 | [5 empty] | Y |  |  | Not Shared
1200 | 2005-11-28 | 702F6501 | E-MIO | CIN | Speed Bk3 Limiting Equipment | Upgrade 2000A 138kV breaker & switch and any other Bk3 limiting equipment. Replace any equipment that would limit the 345/138 xfr to less than the hot spot rating of 520 MVA. | IN |  |  | Cinergy study results using a 2014 model indicate overloading of the Speed transformer under normal and single contingency conditions. For normal conditions, with no contingency, the loading on Speed Bk3 was 485 MVA or 101% of the 478 MVA emergency rating. The highest loading caused by a Cinergy contingency is the outage of the Gibson to Bedford 34506 line which also results in the outage of Bedford 345-138 Bk5 due to the breaker configuration at Bedford. This results in a loading of 518 MVA or 108% of the emergency rating. The highest single contingency loading on Speed Bk3 is caused by an LGEE single contingency of the Buckner to Middletown 345 kV line. The resulting loading on Speed Bk3 is 555 MVA or 116% of its emergency hot spot rating. Initial results from the MISO MTEP06 study also indicate that the Speed transformer will be overloaded. This study is using a 2011 model. The loading on the Speed transformer in the base case is 446 MVA (93%). The contingency loading is 476 MVA (99%) for the Cinergy contingency and 506 MVA (105%) for the LGEE contingency. There are several other contingencies in both the Cinergy studies and the MISO study that cause the Speed transformer to overload. The two contingencies listed above cause the highest loading. | [14 empty] | 2005-11-28 | [5 empty] | Y |  |  | Not Shared
1201 | 2005-11-28 | 804C5822 | E-MIO | CIN | Oakland City to Princeton 100C Uprate | Uprate 13863 to 100C operating temperature from Oackland City to Princeton by adding 3 structures. New limit 1200A terminal equipment. | IN |  |  | This project is a cost effective way to increase capacity to a portion of the system that is historically constrained. The 13863 line will be uprated from 80C to 100C operating temperature with installation of three structures. | [14 empty] | 2005-11-28 | [5 empty] | Y |  |  | Not Shared
1242 | 2006-03-27 | 604F6524 | E-MIO | CIN | Linden Ethanol | Install 1200A switch in 13819 line for new Ethanol plant between Crawfordsville and Tipmont Concord Jct | IN |  |  | New Customer | [20 empty] | Y |  |  | Not Shared
1243 | 2006-03-27 | 104E7901 | E-MIO | CIN | Port Union to Allen 69kV | Construct new 69kV line from Port Union to Allen. | OH |  |  | 69kV line loading and voltage problems. | [20 empty] | Y
1244 | 2006-03-27 |  | E-MIO | CIN | Cayuga to Frankfort 23013 Wave Trap Upgrade | Upgrade wave traps at Cayuga and Frankfort to increase line rating to 797 MVA. | IN |  |  | Under south to north transfer conditions the outage of the Jefferson to Rockport 765 line or the Jefferson to Greentown 765 line will cause the 23013 to overload. | [20 empty] | Y |  |  | Not Shared
1245 | 2006-03-27 |  | E-MIO | CIN | Frankfort Jefferson to Potato Creek new 69kV Line | Construct new 69kV line from Frankfort Jefferson to new Potato Creek switching station. | IN |  |  | 69kV capacity. | [20 empty] | Y
1246 | 2006-03-27 | 602G6548 | E-MIO | CIN | Five Points 23030 Wave Trap | Replace 800A wave trap with a 2000A wave trap. Increase line rating for Five Points to Geist 230kV line. | IN |  |  | Under high load scenarios the loss of the Noblesville to Geist 23007 circuit or the loss of the Noblesville Bk11 345/230kV transformer causes the 23030 to overload. | [20 empty] | Y |  |  | Not Shared
1248 | 2006-03-27 | X02C8677 | E-MIO | CIN | Miami Fort GT 21.6MVAR 69kV capacitor | Install 21.6MVAR 69kV capacitor | OH | [23 empty] | Y
1249 | 2006-03-27 | 602G6621 | E-MIO | CIN | Frankfort 230 36MVAR 69kV capacitor | Install 36 MVAR 69kV capacitor | IN |  |  | Increase system reactive power resources and provide voltage support. | [20 empty] | Y
1250 | 2006-03-27 | X02C8675 | E-MIO | CIN | Kings Mills 28.8 MVAR 69kV capacitor | Install 28.8 MVAR 69kV capacitor. | OH |  |  | This project is required to insure adequate voltage under system normal and outage contingencies on the portion for the 69 kV system supplied by Port Union Substation, Warren Substation and Feeder 3869. It will also provide additional system reactive power resources to lessen the Cinergy system reactive power import. | [20 empty] | Y
1251 | 2006-03-27 |  | E-MIO | CIN | Kokomo Highland Park to Noblesville 23008 Wave Trap Upgrade | Replace 800A wave traps with 2000A wave traps at Kok HP and Noblesville. Increase 230kV line rating from Kok HP to Carmel 146th St Jct to Noblesville. | IN |  |  | Under S to N transfer conditions the loss of the Greentown to Jefferson 765 circuit causes the 23008 to overload. Under high load scenarios the loss of the Noblesville Bk11 345/230kV transformer causes the 23008 to overload. | [20 empty] | Y |  |  | Not Shared
1252 | 2006-03-27 | 602C5687 | E-MIO | CIN | Kokomo Highland Park 23028 Wave Trap | Replace 800A wave trap with a 2000A wave trap. Increase 230kV line rating to Thorntown. | IN |  |  | Under S to N transfer conditions the loss of the Greentown to Jefferson 765 circuit causes the 23008 to overload. | [20 empty] | Y |  |  | Not Shared
1253 | 2006-03-27 | 502G6547 | E-MIO | CIN | Noblesville 23007 Wave Trap | Replace 800A wave trap with a 2000A wave trap. Increase line rating for Noblesville to Geist 230kV line. | IN |  |  | Under high load scenarios the loss of the Five Points to Geist 23030 circuit or the loss of the Carmel 146th St 230/69kV transformer causes the 23007 to overload. | [20 empty] | Y |  |  | Not Shared
1254 | 2006-03-27 | 704G6587 | E-MIO | CIN | Charletown to CMC new 138kV line | Construct 8.5 mi. of 138kV line from Charlestown to CMC. | IN |  |  | The Clark Maritime Center (CMC) is an industrial park in Jeffersonville, IN which is served from a two mile 138kV tap line. The load served from the substation in this industrial park has grown to nearly 30 Mw. Recently, there have been enquiries from businesses interested in locating their production facilities here. In the next five years the load could grow to over 50 Mw which would be at risk of a 138kV line outage. The purpose of this project is to construct an alternate feed into this industrial park as a means for reserving this large load. | [20 empty] | Y |  |  | Not Shared
1255 | 2006-03-27 | 302G8835 | E-MIO | CIN | Covington 138/13 | Construct new 138/13 kV substation | KY |  |  | Distribution capacity | [20 empty] | Y
1260 | 2006-07-05 | 103G8856 | Central | CIN | Obannonville | 60MVA 138/34kV substation loop 5489 into sub. | OH |  |  | Distribution capacity |  |  | Not required | [11 empty] | 2006-07-05 | [5 empty] | Y
1261 | 2006-07-05 | 603B5453 | Central | CIN | Lafayette Shadeland | 22 MVA sub | IN |  |  | Distribution capacity |  |  | Not required | [11 empty] | 2006-07-05 | [5 empty] | Y
1262 | 2006-07-05 | 702G6641 | Central | CIN | HE Durgee Rd | HE 138/12 kV substation. | IN |  |  | Distribution capacity |  |  | Not required | [11 empty] | 2006-07-05 | [5 empty] | Y
1263 | 2006-07-05 | EDWPIGCC | Central | CIN | Edwardsport IGCC | Provide 345 and/or 138 kV interconnection for Edwardsport IGCC plant. | IN |  |  | Needed to connect Edwardsport IGCC generation to the transmission system. |  |  | Not required | [11 empty] | 2006-07-05 | [5 empty] | Y
1264 | 2006-07-05 | 702G6714 | Central | CIN | Speed | Replace existing 345/138 transformer at Speed with a new transformer rated at 3,000A or higher. | IN |  |  | Existing Speed 345/138 transformer overloaded for the loss of LGEE Mill Creek to Paddys West 345 kV line in MTEP06 analysis. |  |  | Not required | [11 empty] | 2006-07-05 | [5 empty] | Y
1265 | 2006-07-05 | 502G6690 | Central | CIN | Geist 69kV Cap 2 | Add a second 69kV 36MVAR cap bank at Geist | IN |  |  | Increase system reactive power resources and provide voltage support. |  |  | Not required | [11 empty] | 2006-07-05 | [5 empty] | Y
1266 | 2006-07-05 | 502G6689 | Central | CIN | Hortonville 69kV Cap | Install 69kV 36MVAR cap bank at Hortonville | IN |  |  | Increase system reactive power resources and provide voltage support. |  |  | Not required | [11 empty] | 2006-07-05 | [5 empty] | Y
584 | 2005-06-15 | 584 | N-NM | DPC/XEL | Genoa-Coulee 161 kV line upgrade | Genoa-Coulee 161 kV line upgrade | WI | [23 empty] | Y |  |  | Not Shared
1025 | 2005-08-31 | Mesaba Energy | N-NM | EEI | Mesaba Energy Project (Excelsior Energy Inc) | Mesaba Energy project generator outlet lines | MN |  |  | Required for G519 or G477 (alternative) |  |  | Required |  | 0 | [9 empty] | 2005-08-31 | [5 empty] | Y |  |  | Service
615 | 2005-07-11 |  | E-MIO | FE | Galion 345/138 kV transformer prep | Galion 345/138 kV transformer prep | OH |  |  |  |  | Approved | Not Required |  | 0% | [12 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
616 | 2006-03-14 |  | E-MIO | FE | Crissinger - Tangy 138 kV line | Crissinger - Tangy 138 kV line | OH |  |  |  |  | Approved | Obtained |  | 5% | [7 empty] | FE - Paul Gerber |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
890 | 2005-07-06 |  | E-MIO | FE | North Medina Substation | Add a new 345/138kV substation at the junction of the Star-Carlisle 345kV and Star-West Akron #2 138kV lines | OH | [17 empty] | 2005-07-06 | [5 empty] | Y |  |  | Share
1061 | 2005-11-18 | F23 |  | FE | F23, 36560-02 | Net: Minor system protection modifications at Napoleon Sub. Int: None | OH |  |  | http://www.midwestiso.org/plan_inter/documents/F23-Napoleon_SIS_FS.pdf | [13 empty] | http://www.midwestiso.org/plan_inter/documents/F23-Napoleon_SIS_FS.pdf | 2000-02-04 | [5 empty] | Y
1062 | 2005-11-18 | F24 |  | FE | F24, 36560-01 |  | OH |  |  | http://www.midwestiso.org/plan_inter/documents/F24-Bowling_Green_SIS_FS.pdf | [13 empty] | http://www.midwestiso.org/plan_inter/documents/F24-Bowling_Green_SIS_FS.pdf | 2000-02-04 | [5 empty] | Y
1070 | 2005-11-18 | F33 |  | FE | F33, 36665-02 | Net: None. Int: Breaker replacements | OH |  |  | http://www.midwestiso.org/plan_inter/documents/F33-Fremont_SIS.pd | [13 empty] | http://www.midwestiso.org/plan_inter/documents/F33-Fremont_FS_Addendum.pdf | 2000-05-19 | [5 empty] | Y | 2003-05-01
1132 | 2005-11-18 | F221 |  | FE | F221, 37473-01 | Net: Minor sub station modifications. Int: - | OH |  |  | Required for generator interconnection request | [13 empty] | http://www.midwestiso.org/plan_inter/documents/F221_Facility_Study_Report.pdf | 2002-08-05 | [5 empty] | Y
596 | 2005-06-15 |  | N-NM | GRE | Vermillion River - Empire 115 kV line | Vermillion River - Empire 115 kV line | MN |  |  | Voltage concerns on contingency |  |  |  |  | 0 | [15 empty] | Y |  |  | Excluded
597 | 2005-06-15 |  | N-NM | GRE | Parkers Lake - Plymouth - Elm Creek 115 kV line | Parkers Lake - Plymouth - Elm Creek 115 kV line | MN |  |  | Voltage concerns and line overloading on contingency |  |  |  |  | 20 | [12 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
599 | 2005-06-15 |  | N-NM | GRE | Crooked Lake - Enterprise Park 115 kV line | Crooked Lake - Enterprise Park 115 kV line | MN |  |  | Line overloading on contingency | [17 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
600 | 2005-06-15 |  | N-NM | GRE | Baxter - Southdale 115 kV line | Baxter - Southdale 115 kV line | MN |  |  | Line overloading in Brainerd area | [17 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
601 | 2005-06-15 |  | N-NM | GRE | Mud Lake - Wilson Lake 115 kV line | Mud Lake - Wilson Lake 115 kV line | MN |  |  | Voltage concerns on contingency | [20 empty] | Y |  |  | Excluded
602 | 2005-06-15 |  | N-NM | GRE | Brownton - McLeod 115 kV line | Brownton - McLeod 115 kV line | MN |  |  | Voltage concerns on contingency | [17 empty] | 2005-06-16 |  |  | Y
753 | 2005-06-15 |  | N-NM | GRE | Hubbard 115 kV 27 MVAR Capacitor | Hubbard 115 kV 27 MVAR Capacitor | MN |  |  | Voltage concerns system intact and contingency | [17 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
891 | 2005-06-27 |  | N-NM | GRE | Elk River 230-69 kV transformer #2 | Add a 2nd 230-69 kV transformer at Elk River | MN |  |  | Load Serving | [14 empty] | 2005-06-27 | [5 empty] | Y
892 | 2005-06-27 |  | N-NM | GRE | Parkwood 230-69 kV transformer #2 | Add a 2nd 230-69 kV transformer at Parkwood | MN |  |  | Load Serving | [14 empty] | 2005-06-27 | [5 empty] | Y
1018 | 2004-12-23 |  | N-NM | GRE | Little Falls - Pierz conversion to 115 kV | Convert Little Falls - Pierz 34 kV line to 115 kV operation | MN | [17 empty] | 2004-12-23 | [5 empty] | Y |  |  | Not Shared
1026 | 2005-06-27 | A125, A130 | N-NM | GRE | Linwood 230-69 kV transformer | Required for TSR A125 and A130 | MN |  |  | Required for A125 and A130 TSR studies | [20 empty] | Y
1065 | 2005-11-18 | G034 |  | GRE | G034, 36632-01 |  | MN |  |  | http://www.midwestiso.org/plan_inter/documents/G034_Deliverability_Study_Report.pdf | [14 empty] | 2000-04-16 | [5 empty] | Y | 2003-04-01
1140 | 2005-11-18 | G272 |  | GRE | G272, 37595-01 | Net: The Transmission Owner shall construct a transmission structure with a 2-way, load break, manual operated, 1200 amp or higher, 115 kV switch (operated at 69 kV) and a tap line to the Customer's termination structure.. Int: none | MN |  |  | http://www.midwestiso.org/plan_inter/documents/generation_inter/G272_IES_Report.zip | [13 empty] | http://www.midwestiso.org/plan_inter/documents/generation_inter/G272_IFS_Report.pdf | 2002-12-05 | [5 empty] | Y | 2005-12-01
286 | 2005-07-29 | 281 | N-NM | GRE/MPC/XEL/OTP/MP/W | TIPS 345 kV Line | Alexandria - Benton County 345 ckt 1, Sum rate 720 | MN |  |  | Winter Peak conditions with heavy transfers north to Manitoba are showing some voltage stability concerns in the Red River Valley - This project will alleviate these concerns | Red River Valley / West Central Minnesota Transmission Improvement Planning Study (RRV/WMN TIPS) | Pending | Pending | Low | 0% | Coal Creek - Underwood - Harvey - Prairie 345 kV Line; Garrison - Max - Minot - Rugby - Drayton 230 kV Line; Bismarck - Jamestown - Fargo 345 kV Line; Boswell - Wilton 230 kV Line; Dorsey - Karlstad - Winger 345 kV Line; Fargo - Moorhead - Morris - Granite Falls - Blue Lake 345 kV Line; Watertown - Granite Falls - Blue Lake 345 kV Line | [7 empty] | This project is the result of the TIPS report which identified voltage collapse issue in the Red River Valley area of Minnesota. This line is need to provide additional MVAR support from the Sherco/Monticello generation areas. | [6 empty] | Y
287 | 2005-07-29 | 281 | N-NM | GRE/MPC/XEL/OTP/MP/W | TIPS 345 kV Line | Maple River - Alexandria 345 ckt 1, Sum rate 720 | MN | ND | 0.05 | Winter Peak conditions with heavy transfers north to Manitoba are showing some voltage stability concerns in the Red River Valley - This project will alleviate these concerns | Red River Valley / West Central Minnesota Transmission Improvement Planning Study (RRV/WMN TIPS) | Pending | Pending | Low | 0% | Coal Creek - Underwood - Harvey - Prairie 345 kV Line; Garrison - Max - Minot - Rugby - Drayton 230 kV Line; Bismarck - Jamestown - Fargo 345 kV Line; Boswell - Wilton 230 kV Line; Dorsey - Karlstad - Winger 345 kV Line; Fargo - Moorhead - Morris - Granite Falls - Blue Lake 345 kV Line; Watertown - Granite Falls - Blue Lake 345 kV Line | [7 empty] | This project is the result of the TIPS report which identified voltage collapse issue in the Red River Valley area of Minnesota. This line is need to provide additional MVAR support from the Sherco/Monticello generation areas. | [6 empty] | Y
1033 | 2005-01-03 |  | N-NM | GRE/OTP | Silver Lake 230/41.6 kV transformer | Silver Lake 230/41.6 kV transformer | MN | [23 empty] | Y
603 | 2005-06-15 |  | N-NM | GRE/XEL | Alexandria - West St. Cloud 115 kV line | Alexandria - West St. Cloud 115 kV line | MN |  |  | 69 kV voltage concerns on contingency | [20 empty] | Y |  |  | Share
204 | 2005-06-15 | 183 | E-MIO | HE | Tapline 138 to Buena Vista, Batesville, & North Charleston | Buena Vista-Tapline 138, Batesville-Tapline 138, North Charleston-Tapline 138 | IN | [20 empty] | 2003-06-25 |  |  | Y |  |  | Not Shared
40 | 2005-11-17 | IPL-05 | E-MIO | IPL | Cumberland-Julietta-Indian Crk 138kV Line | Add new 138kV Line from Cumberland to Julietta to Indian Creek | IN |  |  | SE Indianapolis area distribution support. The distribution capacity in this area is not adequate to support the load growth. Thus, two new substations are planned to serve distribution load. To support these new substations, a new transmission line is planned in this area. |  | Budgeted | Not Required | [14 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
893 | 2005-07-06 | IPL-02 | E-MIO | IPL | North 138 kV 150 MVAR Capacitor | Capacitor Bank SizeUpgrade: North 138 kV 100 MVAR To 150 MVAR | IN |  |  | Indianapolis Area Voltage Support. |  | Pending | [12 empty] | 2005-07-06 | [5 empty] | Y |  |  | Not Shared
894 | 2006-06-26 | IPL-03 | E-MIO | IPL | Pike 138 kV 150 MVAR Capacitor | New Capacitor Bank: Pike 138 kV 150 MVAR | IN |  |  | Indianapolis Area Voltage Support. |  | Approved | [12 empty] | 2005-07-06 | [5 empty] | Y |  |  | Not Shared
895 | 2006-06-26 | IPL-04 | E-MIO | IPL | Georgetown To Northeast 138kV Loop-In | Loop Georgetown to Northeast 138kV Line Into North Substation | IN |  |  | NERC Category C Outages In The NE Indianapolis Area. |  | Approved | [12 empty] | 2005-07-06 | [5 empty] | Y |  |  | Not Shared
897 | 2005-07-06 | IPL-07 | E-MIO | IPL | Thompson 345/138kV Autotransformer | Add new 345/138kV autotransformer at Thompson Substation | IN |  |  |  |  | Pending | [12 empty] | 2005-07-06 | [5 empty] | Y
503 | 2005-08-10 | p2-48 | E-MIO | ITC | Wixom-Quaker 230 | Project to add 345/230 kV transformer at Wixom, un-six-wire Wixom to Hancock 120 kV ckt, decommission Hancock to Quaker 120 kV ckt, add 230/120 kV transformer at Quaker (on new bus), create new 230 kV ckt from Wixom to Quaker, and reconductor 4 miles of the existing Hancock to Southfield 120 kV circuit. | MI |  |  | Eliminates overloading the Wixom 345/120 xfmr for the loss of the Quaker 345/120 and vice versa. Project also provides some relief to the hines 230/120 kV Xfmr |  | Pending | Pending |  | 0% | [12 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
509 | 2005-08-10 | p2-56 | E-MIO | ITC | Lenox Station | Belle River-Lenox and Lenox-Jewel 345 kV lines, Lenox 345/120 kV transformer, and 120 kV station that ties together several 120 kV lines in the area. (St Clair, Victor, Augusta tap, Grayling 1 & 2). Was New Haven, named changed to Lenox. | MI |  |  | Solves voltage problems at Malta Victor and Grayling for the loss of St. Clair-Jacob 120 kV. Relieves loadings on the Stephens 345-120 kV transformers which overload for loss of the other. Relieves loading on Bismarck-Stephens 120 kV for the shutdown plus contingency of both Stephens 345-120 kV transformers. | 2005 ITC Capital Project Presentation for MISO.ppt | Pending | Obtained | Low | 10% | [9 empty] | 2004-10-08 | 2004-11-12 | Y | 2004-11-15 |  |  | Y |  |  | Excluded
518 | 2005-08-10 | p2-66 | E-MIO | ITC | Bismark-Golf | Bismark-Golf 120 kV line: create a 120 kV station at Golf and build a new 120 kV line from Bismarck to Golf. | MI |  |  | Solves potential voltage stability issues in the Macomb area associated with St. Clair 120 kV generation outages with the loss of Macomb-Stephens 120 kV. Solves overloads in the Macomb, Boyne St. Clair loop for single circuit outages as well as common tower outages. Also provides for the interconnetion of a third distribution transformer at Golf. | 2005 ITC Capital Project Presentation for MISO.ppt | Approved | Obtained | Low | 80% | [6 empty] | Branches with multiple status ? |  |  | 2004-10-08 | 2004-11-12 | Y | 2004-11-15 |  |  | Y |  |  | Excluded
578 | 2005-08-10 | 578 | E-MIO | ITC | DVARs at Wyatt and Lee | Installs DVARs at Wyatt Station and Lee Station | MI |  |  | Relieves voltage stability\low voltage issues in the thumb loop for the shut down of Harbor Beach Power Plant+ N-1 | 2005 ITC Capital Project Presentation for MISO.ppt | Approved | Obtained | Low | 50% | [9 empty] | 2004-10-08 | 2004-11-12 | Y | 2004-11-15 |  |  | Y |  |  | Excluded
586 | 2005-08-10 |  | E-MIO | ITC | Stephens - Erin 120 kV line #3 | Constructs new 120 kV Cable from Stephens to Erin | MI |  |  | Relieves severe overloads of circuits in the Erin loop for the common tower failure of Erin-Stephens 1 and 2. Reduces the risk of dumping 300+ MW of load for a single outage |  | Pending | Pending |  | 0% | [15 empty] | Y |  |  | Share
686 | 2005-08-10 | ITC7 | E-MIO | ITC | Majestic 345/120 kV switching station | Create a Majestic-Madrid 120 kV circuit by un-six wiring the existing Majestic-Madrid 345 kV circuit and connecting the available conductor to a new 120 kV bus and position off the Madrid 120 kV bus and the new 120 kV substation via a 345/120 kV transformer at the Majestic station. Poroject also requiresbus expansions at both Madrid 120 kV and 345 kV stations | MI |  |  | Solves the voltage problem in the Genoa 120 kV area for the lost of a N-1 condition at high transfers from METC into ITC |  | Pending | Pending |  | 0% | [15 empty] | Y |  |  | Share
692 | 2005-08-10 | ITC8 | E-MIO | ITC | Bismark-Troy 345 | Creates a Bismarck-Troy 345 kV line & a Troy 345/120 kV transformer. | MI |  |  | Relieves circuit loading on lines in the central part of the ITC system which overload for various N-1 and common tower failures |  | Pending | Pending |  | 0% | [15 empty] | Y |  |  | Share
694 | 2005-06-15 | ITC9 | E-MIO | ITC | Saratoga Station | Saratoga 345/120 kV switching station | MI | [23 empty] | Y |  |  | Share
900 | 2005-08-10 | aa | E-MIO | ITC | Duvall Tie | Construct a section breaker at Duvall station to tie buses 101 and 102 together. Also construct addition 0.8 miles of wood poles to establish a Hager to Hines 120 kV circuit | MI |  |  | Relieves the Hines 230/120 kV transformer for pre and post contingency conditions |  | Pending | Pending |  | 0% | [15 empty] | Y |  |  | Not Shared
902 | 2005-08-10 | cc | E-MIO | ITC | Greenwood 345/120 Xmfr | Puts in new 345/120 kV Xfmr at Greenwood and constructs new Greenwood-Wabash 120 kV and Greenwood-Adams 120 kV | MI |  |  | New transformer is designated a new service spare and removes SOP of droppign the 785 MW gen unit at Greenwood for the loss of the 3-ended 345 kV BLRPP-GRNEC-PONTC |  | none | [18 empty] | Y |  |  | Share
903 | 2005-08-10 | dd | E-MIO | ITC | Stephens - Bismark | Creates a Bismark-Stephens 230 kV line with a 230/120 kV Xfmr at Stephens, and also builds a new Stephens-Redrun 120 kV | MI |  |  | Bismark-Stephens 120 kV circuit overloads for loss of the 2 Stephens 345/120 Xfmrs at load levels of 85% peak |  | none | [18 empty] | Y |  |  | Share
904 | 2005-08-10 | ee | E-MIO | ITC | Wyatt Station | Creates Wyatt Station and cuts Bad Ax-Harbor Beach 120 and Seaside-Sandusky 120 into the new station. | MI |  |  | Relieves voltage stability\low voltage issues in the thumb loop for the shut down of Harbor Beach Power Plant+ N-1 |  | Pending | [18 empty] | Y |  |  | Not Shared
905 | 2005-08-10 | ff | E-MIO | ITC | Marysville Decommissioning | Decommission Marysville Station, expand Bunce Creek Station creating new Bunce Creek - Cypress, Bunce Creek - Menlo, Bunce Creek - Wabash 2 120 kV lines. | MI |  |  | Allows for the removal of Marysville Station and its associated equipment from the ITC system as the station and power plant are planned to be shutdown. Also allows for the interconection of 2 distribution transformers at Bunce Creek to replace capacity lost at Marysville. |  | none |  |  | 0% | [15 empty] | Y |  |  | Not Shared
907 | 2005-08-10 | hh | E-MIO | ITC | Goodison Station | Build Goodison Station, with a Belle River-Goodison 345 kV, Pontiac-Goodison 345 kV, new 345/120 kV Xfmr, new Pontiac-Goodison 120 kV line, Goodison-Tienken 120 kV, Sunbird-Goodison 120 kV, and Tienken-Spokane 120 kV. | MI |  |  | Relieves circuit loading on the Pontiac Transformers as well as on the lines out of Pontiac which overload for N-1 conditions. Also relieves loading on the Bloomfield-Hamlin 120 kV line which overloads for the loss of the Jewell-Spokane 230 kV line. |  | Pending |  |  | 0% | [15 empty] | Y |  |  | Share
908 | 2005-08-10 | ii | E-MIO | ITC | Lulu Station | Phase One - Construct a 345 kV switching station at the Lulu site, including 8 345 kV breakers and Cut in the Majestic - Lemoyne 345 kV circuit into new Lulu station and the Milan-Allen Junction-Monroe 3-4 345 kV circuit into new Lulu station. Phase Two - Split the Lulu to Lemoyne 345 kV circuit into a Lulu to Monroe 1-2 345 kV circuit and a Leymoyne to Monroe 3-4 345 kV circuit, creating a new 3 mile 345 kV double circuit tower line. | MI |  |  | Proposed as part of the Tier One of the Michigan Capacity Needs study projects to increase import capability into the ITC service teritory. Also breaks up a long three ended 345 kV circuit. |  | none |  |  | 0% | [15 empty] | Y |  |  | Share
909 | 2005-08-10 | jj | E-MIO | ITC | 230 kV Northwest | Tap one of the METC Thetford to Hampton 345 kV circuits west of the ITC Atlanta 120 kV station, build a new 2.3 mile 345 kV line from the tap to the Atlanta station, install a 345/230 kV transformer at Atlanta, build a new 13.6 mile 230 kV circuit from Atlanta to the Tuscola station, install a 230/120 kV transformer at Tuscola, convert 22.5 mile 120 kV circuit from Tuscola down to a new 345 kV switching station at the Hunters Creek station to 230 kV, install a 345/230 kV transformer and a 230/120 kV transformer at Hunters Creek, and tap the Belle River to Blackfoot 345 kV circuit at Hunters Creek. | MI |  |  | Proposed as part of the first phase of Tier One of the Michigan Capacity Needs study projects to increase import capability into the ITC service teritory. Also helps to mitigate double circuit tower overloads during heavy west to east flows. |  | none |  |  | 0% | [15 empty] | Y |  |  | Share
910 | 2005-08-10 | kk | E-MIO | ITC | Coventry Station upgrade | Constructs new Coventry-Cody 230 kV line using the same right-of-way currently occupied by the Coventry-Cody 120 kV circuit. Project involves constructing a new 345/230 kV tranformer at Coventry along with a 230/120 kV transformer at Cody. Project also invloves expansion of the Coventry 345 kV station. | MI |  |  | Relieves the Coventry 345/120 kV transformer for pre and post contingency conditions |  | Pending |  |  | 0% | [15 empty] | Y |  |  | Share
911 | 2005-08-10 | ll | E-MIO | ITC | Placid 345/120 Xfmr | Construct second 345/120 kV transformer at the Placid station. Project involves expansions at both Placid 120 kV and 345 kV stations | MI |  |  | Project solves the voltage problems in the Placid area for the loss of a N-1 condition |  | Pending |  |  | 0% | [15 empty] | Y |  |  | Share
1011 | 2006-07-05 | ITC22 | E-MIO | ITC | Durant-Genoa 120 kV | Builds a new 120 kV Durant sub-station with a new circuit from Genoa to Durant, and also breaks up 3-ended Prizm-Proud-Placid 120 kV line | MI |  |  | This line is being built to address customer requests to improve reliability to the Prizm sub-station and provide for future load growth in the area |  | Pending |  |  | 0% | [6 empty] | Prizm-Nolan is now planned to go from Prizm-Genoa (T. Vitez 2/10/06). |  |  | 2005-08-10 | [5 empty] | Y |  |  | Share
1012 | 2005-08-10 | zz | E-MIO | ITC | Wyane - Newburg Split | Split existing six-wired 120 kV circuit from Wayne to Newburg creating a new 2.8 mile 120 kV circuit. | MI |  |  | Proposed as part of the Tier One of the Michigan Capacity Needs study projects to increase import capability into the ITC service teritory. |  | Pending |  |  | 0% | [9 empty] | 2005-08-10 | [5 empty] | Y |  |  | Not Shared
1172 | 2005-11-18 | G350 |  | ITC | G350, 37790-01 |  | MI |  |  | Required for generator interconnection request | [14 empty] | 2003-06-18 | [5 empty] | Y | 2007-09-30
246 | 2005-06-15 | TRN.410.02 | N-Nebraska | LES | North Tier 115 kV, Phase II | NW68th & Holdrege - NW 12th & Arbor 115 ckt 1, Sum rate 373 | NE |  |  | New NW40th & Alvo, Substation, load supplying 115/12kV |  | Budgeted | Required |  | 0% | [6 empty] | Project ID 246 and 804 are 115kV lines that will be double-circuited with the proj. 247 so their construction is also committed to | [5 empty] | 2003-06-25 |  |  | Y |  |  | Excluded
247 | 2005-06-15 | TRN.610.06 | N-Nebraska | LES | North Tier 345 kV | A 26-mile 345-kV line extending from the LES owned Wagener Substation to the LES owned NW68th & Holdrege Substation. | NE |  |  | Load serving needs of LES, and as an LES project that has its in-service date tied to the in-service date of OPPD’s Nebraska City Unit 2 Project. | P0247_LES_North_Tier_345kV.doc | Budgeted | Required | Medium | 0% | The existing NPPD owned Pauline - Moore 345-kV line was an alternative in the form of a Pauline - NW68th & Holdrege 345-kV line. | [5 empty] | some possibility of not being completed in 2008 |  | A 26-mile 345kV line that is an LES project but is being added with the transmission facilities associated with the future OPPD owned coal-fired Nebraska City Unit #2 (i.e., nominal net output of 700 MW). Roughly 5-miles of the 345kV line was constructed several years ago as part of a double-circuit with a 115kV line, although the 345kV line was not energized. |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
590 | 2005-06-15 | TRN.440.05 | N-Nebraska | LES | 40th & Rokeby Transmission | 56th & Pine Lake - 40th & Rokeby - 27th & Pine Lake 115 kV line, Sum rate 373 | NE |  |  | New 40th & Rokeby substation, load supplying 115/12 kV sub |  | Approved | Not Required |  | 0% | [12 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
804 | 2005-07-08 | TRN.440.07 | N-Nebraska | LES | Rebuild North Tier 115 kV | Rebuild part of 19th & Alvo - 70th & Bluff 115 ckt 1, Sum rate 363 | NE |  |  | Rebuild storm damaged line, double-circuit with new 345kV line | [20 empty] | Y |  |  | Share
805 | 2005-07-08 | TRN.610.03 | N-Nebraska | LES | NW68th & Holdrege 345/115 kV #2 | Add 2nd NW68th & Holdrege 345/115 kV transformer, rate 336 MVA | NE |  |  | Increase 345/115 transformer capacity around Lincoln | [20 empty] | Y |  |  | Share
25 | 2005-07-08 | 1010 | E-IOK | LGEE | Trimble Generator #2 outlet | Construct 2.8 mi of double circuit 345 kV line from Trimble Co to Cinergy's Ghent to Speed 345 kV line and add two 345 kV line exits at Trimble Co. | KY | IN | 0.3 | Overload of Trimble Co to Middletown 345 kV line with outage of Buckner to Middletown 345 kV line + MC4 | [8 empty] | 13179000 | [11 empty] | Y | 2009-12-31 |  | Service
309 | 2005-07-08 | 487 | E-IOK | LGEE | Lake Reba Tap to Delvinta 161 kV line--replace wavetrap | Replace the 161 kV, 800A wave trap associated with the Lake Reba Tap to Delvinta 161 kV line. | KY |  |  | Overload of Lake Reba Tap to Delvinta 161 kV line with outage of JK Smith to Powell Co 138 kV line + MC4 | [8 empty] | 20000 | [11 empty] | Y | 2007-11-30 |  | Not Shared
313 | 2005-06-15 | LGEE3 | E-IOK | LGEE | Middletown - Buckner 345 kV line | Middletown - Buckner 345 ckt 1, Sum rate 1066 | KY |  |  |  |  | Budgeted | Not Required | [14 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
314 | 2005-07-08 | 543 | E-IOK | LGEE | Lake Reba Tap - JK Smith (EKPC) 138 | Replace the 954 kcm ACSR line riser at Lake Reba Tap associated with the Lake Reba Tap-JK Smith 138 kV line with 1272 kcm ACSR or equivalent equipment. | KY |  |  | Overload of Lake Reba Tap to JK Smith 138 kV line with outage of EKPC Fawkes to JK Smith 138 kV line + Br3 | [8 empty] | 10000 | [11 empty] | Y | 2009-11-30 |  | Excluded
317 | 2005-07-08 | 364 | E-IOK | LGEE | Mill Creek-Manslick 138 kV line (circuit 3834)--increase MOT | Increase the MOT of the 636 kcm ACSR in the Mill Creek-Manslick 138 kV line (circuit 3834) from 176F to 180F. | KY |  |  | Overload of Mill Creek to Manslick 138 kV line with outage of Middletown to Bluelick 345 kV line + CR6 | [8 empty] | 75000 | [11 empty] | Y | 2007-05-30 |  | Not Shared
928 | 2005-07-08 | 50 | E-IOK | LGEE |  | Replace the 800A wave trap associated with breaker 152-724 at Brown North (Brown North-Pisgah 138 kV) with a 1200A wave trap. | KY |  |  | Overload of Brown North to Pisgah 138 kV line with outage of Ghent to West Lexington to Brown 345 kV line + Gh1 | [8 empty] | 20000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2009-05-30 |  | Not Shared
929 | 2005-07-08 | 64 | E-IOK | LGEE |  | Replace the 500 kcm Cu bus associated with breaker 66-734 at Higby Mill with 750 kcm Cu. | KY |  |  | Overload of Higby Mill 138 kV bus with outage of Brown North to Baker Ln. to Higby Mill 138 kV line + Gh1 | [8 empty] | 20000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2009-05-30 |  | Not Shared
930 | 2005-07-08 | 72 | E-IOK | LGEE |  | Replace 1200A breaker 176-714 at Loudon Avenue with 1600A equipment. | KY |  |  | Overload of Avon EKPC to Loudon Avenue 138 kV line with outage of Ghent to West Lexington to Brown 345 kV line + Br3 | [8 empty] | 160000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2009-11-30 |  | Not Shared
932 | 2005-07-08 | 180 | E-IOK | LGEE |  | Install a second 345/138 kV, 450 MVA transformer at Hardin County. | KY |  |  | Voltage of Elizabethtown #2 69 kV bus with outage of Hardin County 345/138 kV transformer + Sm2 | [8 empty] | 5010000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2007-05-30 |  | Share
933 | 2005-07-08 | 182 | E-IOK | LGEE |  | Upgrade the terminal limit on the Hardin Co 345/138 kV transformer to 448/478 MVA summer normal and emergency and 478/478 MVA winter normal and emergency. | KY |  |  | Overload of Hardin Co 345/138 kV transformer #1 with outage of Hardin Co 345/138 kV transformer #2 + MC4 | [8 empty] | 57000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2010-05-30 |  | Not Shared
934 | 2005-07-08 | 332 | E-IOK | LGEE |  | Increase the MOT of the 556 kcm ACSR in the Brown North-Tyrone 138 kV line from 176F to 212F. | KY |  |  | Overload of Brown North to Tyrone 138 kV line with outage of West Frankfort to Ghent 345 kV line + Gh3 | [8 empty] | 300000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2010-05-30 |  | Not Shared
935 | 2005-07-08 | 349 | E-IOK | LGEE | Blue Lick-Bullitt County 161 kV line--increase MOT | Increase the MOT of the 500 kcm Cu in the Blue Lick-Bullitt County 161 kV line from 176F to 212F. | KY |  |  | Overload of Blue Lick to Bullitt Co 161 kV line with outage of Trimble Co to Clifty Creek 345 kV line + Br3 | [8 empty] | 300000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2006-03-30 |  | Not Shared
936 | 2005-07-08 | 360 | E-IOK | LGEE | Replace 556A on Fawkes KU-Fawkes EKPC Tap section with 795A | Replace the 556 kcm ACSR in the Fawkes KU-Fawkes EKPC Tap section of the Fawkes-Lake Reba Tap 138 kV line with 795 kcm ACSR. | KY |  |  | Overload of Fawkes EKPC tap to Fawkes KU 138 kV line with outage of Fawkes KU to Fawkes EKPC 138 kV line + Br3 | [8 empty] | 75000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2006-05-30 |  | Not Shared
937 | 2005-07-08 | 366 | E-IOK | LGEE |  | Increase the 161 kV capability of the terminal equipment associated with the Blue Lick 345/161 kV transformer to at least 1200A. | KY |  |  | Overload of Blue Lick 345/161 kV transformer with outage of Trimble Co to Clifty Creek 345 kV line + Br3 | [8 empty] | 30000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2005-11-30 |  | Not Shared
938 | 2005-07-08 | 367 | E-IOK | LGEE |  | Install a fourth 345/138 kV, 450 MVA transformer at Middletown. | KY |  |  | Overload of Middletown 448 MVA - 345/138 kV transformer #3 with outage of Middletown 345/138 kV transformer #5 + CR6 | [8 empty] | 5523000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2010-05-30 |  | Share
939 | 2005-07-08 | 375 | E-IOK | LGEE |  | Replace the 1033 kcm ACSR in the Northside-Jeffersonville Jct. section of the Northside-Beargrass 138 kV line (circuit 3882) with 2-954 kcm ACSR. | IN |  |  | Overload of Northside to Jeffersonville Jct. 138 kV line with outage of Northside to Beargrass 138 kV line + CR6 | [8 empty] | 50000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2010-05-30 |  | Not Shared
940 | 2005-07-08 | 394 | E-IOK | LGEE |  | Open the KU-EKPC Goddard 138 kV interconnection. | KY |  |  | of with outage of + | [8 empty] | 0 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2006-11-30 |  | Not Shared
941 | 2005-07-08 | 395 | E-IOK | LGEE |  | Remove the 5% reactor from the Kenton-Rodburn 138 kV line. | KY |  |  | of with outage of + | [8 empty] | 0 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2006-11-30 |  | Not Shared
943 | 2005-07-08 | 402 | E-IOK | LGEE | Reconductor the Ghent-Owen County Tap section of the Ghent-Scott County 138 kV line using 954 kcm ACSR. | Reconductor the Ghent-Owen County Tap section of the Ghent-Scott County 138 kV line using 954 kcm ACSR. | KY |  |  | Overload of Ghent to Owen Co Tap 138 kV line with outage of Ghent to West Lexington to Brown 345 kV + Br3??? | [8 empty] | 240000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2009-12-30 |  | Service
944 | 2005-07-08 | 484 | E-IOK | LGEE |  | Replace the 1200A wave trap at Fawkes associated with the Fawkes-Lake Reba Tap 138 kV line with 1600A equipment. | KY |  |  | Overload of Fawkes to Lake Reba Tap 138 kV line with outage of Fawkes KU to Fawkes EKPC 138 kV line + Br3 | [8 empty] | 20000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2007-11-30 |  | Not Shared
945 | 2005-07-08 | 485 | E-IOK | LGEE |  | Replace the 500 MCM Cu bus at Fawkes associated with the Fawkes-Lake Reba Tap 138 kV line with 750 MCM Cu bus or equivalent. | KY |  |  | Overload of Fawkes to Lake Reba Tap 138 kV line with outage of Fawkes KU to Fawkes EKPC 138 kV line + Br3 | [8 empty] | 20000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2008-11-30 |  | Not Shared
946 | 2005-07-08 | 486 | E-IOK | LGEE |  | Replace the 1200A meter CT at Fawkes associated with the Fawkes-Fawkes EKPC 138 kV line with 1600A equipment. | KY |  |  | Overload of Fawkes KU to Fawkes EKPC 138 kV line with outage of Fawkes to Lake Reba Tap 138 kV line + Br3 | [8 empty] | 30000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2007-11-30 |  | Not Shared
948 | 2005-07-08 | 520 | E-IOK | LGEE |  | Change the CT settings associated with breaker 155-714 at Bardstown (Bardstown-Brown CT) from 600A to 800A. | KY |  |  | Overload of Bardstown to Brown CT 138 kV line with outage of Brown North to Hardin Co to Smith 345 kV line + MC4 | [8 empty] | 3000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2009-05-30 |  | Not Shared
950 | 2005-07-08 | 523 | E-IOK | LGEE |  | Increase the MOT of the Fawkes Tap-Lake Reba Tap section of the Fawkes-Lake Reba Tap 138 kV line from 176F to 212F. | KY |  |  | Overload of Fawkes Tap to Lake Reba Tap 138 kV line with outage of Fawkes KU to Fawkes EKPC 138 kV line + Br3 | [8 empty] | 300000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2009-05-30 |  | Not Shared
951 | 2005-07-08 | 524 | E-IOK | LGEE |  | Replace the 500 MCM CU terminal equipment at Hardinsburg associated with breaker 184-724 (Hardinsburg-Hardin Co 138 kV) with 750 MCM CU equipment. | KY |  |  | Overload of Hardinsburg to Hardin Co 138 kV line with outage of Brown North to Hardin Co to Smith 345 kV line + Br3 | [8 empty] | 20000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2010-05-30 |  | Not Shared
952 | 2005-07-08 | 525 | E-IOK | LGEE |  | AEP taps the Arnold-Delvinta 161 kV line to connect to the Hazard-Leslie 161 kV line. | KY |  |  | of with outage of + | [8 empty] | 0 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2005-11-30 |  | Not Shared
953 | 2005-07-08 | 527 | E-IOK | LGEE |  | Increase the MOT of the 556 kcm ACSR in the Mercer County-Lebanon section of the Brown Plant-Lebanon 138 kV line from 176F to 212F. | KY |  |  | Overload of Mercer Co to Lebanon 138 kV line with outage of Brown North to Alcalde to Pineville 345 kV line + MC4 | [8 empty] | 300000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2009-05-30 |  | Not Shared
954 | 2005-07-08 | 528 | E-IOK | LGEE |  | Increase the summer emergency capability of the metering and relaying CTs at Middletown associated with circuit 4543 to at least 2000 A. | KY |  |  | Overload of Middletown to Buckner 345 kV line with outage of Middletown to Trimble County 345 kV line + MC4 | [8 empty] | 3000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2006-05-30 |  | Not Shared
955 | 2005-07-08 | 529 | E-IOK | LGEE |  | Increase the summer emergency rating of the terminal equipment at Trimble County and Middletown associated with the Trimble County-Middletown 345 kV line (circuit 4541) to at least 2000A. | KY |  |  | Overload of Middletown to Trimble County 345 kV line with outage of Middletown to Buckner 345 kV line + MC4 | [8 empty] | 3000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2006-05-30 |  | Not Shared
956 | 2005-07-08 | 531 | E-IOK | LGEE |  | Increase the maximum verified operating temperature of the Green River (9-724) to Ohio County (85-724) 138 kV line from 160F to 170F. | KY |  |  | Overload of Ohio County to Green River (2) 138 kV line with outage of Ohio County to Green River (1) 138 kV line + Br3 | [8 empty] | 300000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2006-05-30 |  | Not Shared
957 | 2005-07-08 | 534 | E-IOK | LGEE |  | Change the 1200A CT settings at Paddys Run associated with the Paddys West-Paddys Run 138 kV line (circuit 3828) to at least 1500A. | KY |  |  | Overload of Paddys West to Paddys Run 138 kV line with outage of Canal to Paddys West 138 kV line + CR6 | [8 empty] | 3000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2008-05-30 |  | Not Shared
958 | 2005-07-08 | 535 | E-IOK | LGEE |  | Replace the 1000 MCM Cu terminal equipment at Paddys Run associated with the Paddys West-Paddys Run 138 kV line (circuit 3828) with equipment with a summer emergency rating of 1733A or higher. | KY |  |  | Overload of Paddys West to Paddys Run 138 kV line with outage of Canal to Paddys West 138 kV line + CR6 | [8 empty] | 20000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2009-05-30 |  | Not Shared
959 | 2005-07-08 | 538 | E-IOK | LGEE |  | Replace the 600A meter CT at Delvinta associated with the Delvinta-Beattyville-Powell County EKPC 161 kV line with 800A or higher equipment. | KY |  |  | Overload of Delvinta to Beattyville 161 kV line with outage of W Irvine Tap to Delvinta 161 kV line + MC4 | [8 empty] | 20000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2005-11-30 |  | Not Shared
960 | 2005-07-08 | 539 | E-IOK | LGEE |  | Replace the 600A disconnects at Carrollton associated with the Carrollton-Lockport 138 kV line with 1200A or higher equipment. | KY |  |  | Overload of Carrollton to Lockport 138 kV line with outage of W Frankfort to Ghent 345 kV line + Br3 | [8 empty] | 0 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2009-11-30 |  | Not Shared
961 | 2005-07-08 | 544 | E-IOK | LGEE |  | Change the setting of the overload relaying at Dixie associated with the Algonquin-Dixie 138 kV line (circuit 3812) from 640A to at least 800A. | KY |  |  | Overload of Algonquin to Dixie 138 kV line with outage of Paddys Run 138/69 kV transformer + MC4 | [8 empty] | 3000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2010-05-30 |  | Not Shared
962 | 2005-07-08 | 1002 | E-IOK | LGEE |  | Construct 6 mi of 138 kV line using 556 kcm ACSR from EKPC's Avon - Renaker 138 kV line to the 69 kV breaker station at Paris and install a 138/69 kV, 150 MVA transformer at Paris.. | KY |  |  | Overload of Loudon Ave to Avon Tap 69 kV line with outage of Lexington Plant to Joyland 69 kV line + MC4 | [8 empty] | 3434000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2006-05-30 |  | Not Shared
963 | 2005-07-08 | 1004 | E-IOK | LGEE |  | Construct 8 mi of 138 kV line from Virginia City to AEP's Clinch River substation using 556 kcm ACSR and install a 138/69 kV, 120 MVA transformer at Virginia City. | VA |  |  | Overload of Dorchester to Esserville 69 kV line with outage of Dorchester to Norton East 69 kV line + | [8 empty] | 3500 | [5 empty] | 2004-11-23 | 2004-12-15 | Y | 2005-01-19 |  |  | Y | 2006-08-30 |  | Not Shared
964 | 2005-07-08 | 1005 | E-IOK | LGEE |  | Reterminate the Middletown-Ford 69 kV line to 138 kV at Middletown and install a 138/69 kV 150 MVA transformer at Ford | KY |  |  | Overload of Centerfield 138/69 kV 140 MVA transformer with outage of Middletown to Aiken 69 kV line + Gh1 | [8 empty] | 800000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2008-05-30 |  | Not Shared
965 | 2005-07-08 | 1006 | E-IOK | LGEE |  | Construct 3 mi of 161 kV line from the Lake Reba Tap-Delvinta line to West Irvine using 556 ACSR to loop Lake Reba Tap-Delvinta into W Irvine, add 161 kV terminal facilities at West Irvine, replace the 161-69 kV 50 MVA transformer with a 90 MVA and replace | KY |  |  | Addition of ECEP generator with outage of West Irvine 161 kV Tap + | [8 empty] | 1200000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2008-09-30 |  | Service
966 | 2005-07-08 | 1007 | E-IOK | LGEE | Construct 42 mi of 345 kV line from Mill Creek to Hardin County using 2-954 kcm ACSR and add 345 kV line exits at Hardin Co and Mill Creek. | Construct 42 mi of 345 kV line from Mill Creek to Hardin County using 2-954 kcm ACSR and add 345 kV line exits at Hardin Co and Mill Creek. | KY |  |  | Overload of Blue Lick 345/161 kV transformer with outage of Trimble County to Clifty Creek 345 kV line + Br3 | [8 empty] | 56570000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2009-12-30 |  | Service
967 | 2005-07-08 | 1008 | E-IOK | LGEE | Construct 11.8 mi of 138 kV line between West Lexington and Higby Mill using 556 kcm ACSR and add 138 kV line exits at Higby Mill and West Lexington. | Construct 11.8 mi of 138 kV line between West Lexington and Higby Mill using 556 kcm ACSR and add 138 kV line exits at Higby Mill and West Lexington. | KY |  |  | Overload of Brown North to Baker Lane 138 kV line with outage of Brown North to Higby Mill 138 kV line + Gh3 | [8 empty] | 3203000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2009-12-30 |  | Service
968 | 2005-07-08 | 1009 | E-IOK | LGEE | Construct 10.2 mi of 138 kV line between West Frankfort and Tyrone using 795 kcm ACSR and add 138 kV line exits at Tyrone and West Frankfort. | Construct 10.2 mi of 138 kV line between West Frankfort and Tyrone using 795 kcm ACSR and add 138 kV line exits at Tyrone and West Frankfort. | KY |  |  | Overload of West Frankfort to Frankfort East 138 kV line with outage of Ghent to West Lexington to Brown 345 kV line + Br3 | [8 empty] | 4000000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2009-12-30 |  | Service
969 | 2005-07-08 | 1012 | E-IOK | LGEE |  | Construct 14 mi of 138 kV line from Kosmos Cement to Tip Top and add a 138 kV line exit at Tip Top. Rebuild 0.5 mi of the Mill Creek-Kosmos Cement 138 kV line using 795 ACSR and increase the terminal limits at Mill Creek to atleast 143 MVA. | KY |  |  | Voltage of Knob Creek 138 kV bus with outage of Mill Creek to Knob Creek 138 kV line + Sm2 | [8 empty] | 0 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2011-05-30 |  | Not Shared
970 | 2005-07-08 | 1016 | E-IOK | LGEE |  | Reconductor the Hardin County-Etown 138 kV line using 954 kcm ACSR and replace the 500 kcm CU bus and line wire with 750 kcm CU equipment at Etown. | KY |  |  | Overload of Hardin Co to Elizabethtown 138 kV line with outage of Hardin Co 138/69 kV transformer + Br3 | [8 empty] | 40000 | [5 empty] | 2005-07-08 | [5 empty] | Y | 2009-12-30 |  | Service
1063 | 2005-11-18 | G031 |  | LGEE | G031, 36586-01 | Net: None required. Int: 11miles of 161kV from Smithland to Livingston County. Plus cap for a 4.2 MVAR margin at injection point. | KY |  |  | Required for generator interconnection request | [14 empty] | 2000-03-01 | [5 empty] | Y | 2005-09-01
1064 | 2005-11-18 | G032 |  | LGEE | G032, 36586-02 | Net: Sub equipment and a breaker. Cost to be born by gen.. Int: Generator shall construct an 8.5 mile, 138 kV radial circuit from the Generator's Cannelton facility to Kentucky Utilities Co.'s Hancock County Cloverport 138 kV substation. The expected in-service date of the Facility is June 1, 2008. | KY |  |  | Required for generator interconnection request | [14 empty] | 2000-03-01 | [5 empty] | Y | 2008-06-01
1122 | 2005-11-18 | G218 |  | LGEE | G218, 37356-01 | Net: Loop Speed-Ghent 345 kV line to Trimble 345 kV substation. Int: | KY |  |  | http://www.midwestiso.org/plan_inter/documents/G218%20R2%20IE%20%20Report.pdf | [13 empty] | http://www.midwestiso.org/plan_inter/documents/G218%20%20R3%20FS%20Report.pdf | 2002-04-10 | [5 empty] | Y | 2007-01-01
1133 | 2005-11-18 | G243 |  | LGEE | G243, 37384-01 | Net: The Transmission Owner shall construct one 161 kV breaker, including protection and control devices and appurtenant material.. Int: | KY |  |  | http://www.midwestiso.org/plan_inter/documents/G243_IES_Final_Report.pdf | [13 empty] | http://www.midwestiso.org/plan_inter/documents/G243_IFS_Report.pdf | 2002-08-16 | [5 empty] | Y | 2008-12-15
1223 | 2006-02-27 | 111 | E-IOK | LGEE |  | Increase the MOT of the 795 kCM ACSR in the NAS-Dayton Walther Tap section of the Ghent-Dow Corning West 138 kV line to 212°F. | KY |  |  | Overload of NAS to Dayton Walther Tap 138 kV line with outage of Ghent to West Frankfort 345 kV line + MC4 | [13 empty] | Load additions at NAS furnace | 2006-02-01 | 2006-03-14 |  | 2006-04-07 |  |  | Y |  |  | Not Shared
1224 | 2006-02-27 | 1024 | E-IOK | LGEE | Install NAS 345/138 transformer and reconfigure NAS 138 kV lines | Install a 345/138 kV, 450 MVA transformer at NAS. Reconfigure the 138 kV lines into NAS as a single circuit instead of a loop | KY |  |  | Overload of Ghent to NAS 138 kV with outage of Carrollton to Clifty Creek 138 kV + Br3 | [13 empty] | Load additions at NAS furnace | 2006-02-01 | 2006-03-14 |  | 2006-04-07 |  |  | Y |  |  | Not Shared
548 | 2005-08-02 | p2-107 | N-NM | MDU | Bismarck Downtown-East Bismarck 115 kV upgrade to at least 160 MVA | Bismarck Downtown-East Bismarck 115 kV upgrade to at least 160 MVA | ND | [23 empty] | Y |  |  | Not Shared
1008 | 2005-08-02 |  | N-NM | MDU | Bismarck/Mandan 115 kV Circuits transferred from old to new Memorial Bridge | Bismarck/Mandan 115 kV Circuits transferred from old to new Memorial Bridge | ND | [17 empty] | 2005-08-02 | [5 empty] | Y |  |  | Share
1134 | 2005-11-18 | G248 |  | MDU | G248, 37488-01 | Net: The Transmission Owner shall construct two (2) one-way switches with load breaking capability, one on either side of the tap, RTU . Int: Generator shall construct _1_ Remote Terminal Unit as specified by MDU, 1500 ft. 41.6 kV line, specs to be reviewed and approved by MDU, | ND |  |  | http://www.midwestiso.org/plan_inter/documents/G248_Report_20030109.pdf | [14 empty] | 2002-08-20 | [5 empty] | Y | 2003-12-01
1186 | 2005-11-18 | G409 |  | MDU | G409, 38040-01 | Net: The Transmission Owner shall construct 57kV PT with 57kV line attachment, secondary terminated in fused junction box, necessary grounding, and 15kV fuse cutout and 12.47kV main bus attachment. Equipment to be located in Glendive Distribution Substation. Int: none | MT |  |  | http://www.midwestiso.org/plan_inter/documents/G409_R2R3_report.pdf | [14 empty] | 2004-02-23 | [5 empty] | Y | 2004-03-01
1114 | 2005-11-18 | G217 CONS 111 |  | MECS | G217 CONS 111, 37229-02 | Net: Not a valid project (Email from Sherry Tang, 10/14/05). Int: Not a valid project (Email from Sherry Tang, 10/14/05) | MI |  |  | Required for generator interconnection request | [14 empty] | 2001-12-04 | [5 empty] | Y | 2006-07-01
240 | 2005-07-27 | 87 | E-MIO | METC | Garfiled - Hemphill 138 ckt 1 | Garfiled - Hemphill 138 ckt 1, Sum rate 521 | MI |  |  | Overload due to Tower Outage (Thetford-Delaney 138kV & Thetford-Hemphill 138kV). Project delayed beyond June 2009 |  | Not Budgeted | Not Required |  | 0% | [12 empty] | 2003-06-25 |  |  | Y |  |  | Excluded
480 | 2005-07-27 | 112 | E-MIO | METC | Brickyard - Felch 138 kV line | Rebuild 12.8 miles to 795 ACSS | MI |  |  |  |  | Not Budgeted | Not Required |  | 0% | [15 empty] | Y |  |  | Not Shared
481 | 2005-07-27 | 74 | E-MIO | METC | Tallmadge 345/138 kV TB3 transformer #3 | Tallmadge 345/138 kV TB3 transformer #3 addition | MI |  |  | Emergency overload of either Tallmadge transformer for the outage of the other Tallmadge transformer with Cobb 5 in 2007 (102%). Part of third Tallmadge transformer project. |  | Budgeted | Not Required |  | 0% | [6 empty] | and Project 493 | [8 empty] | Y |  |  | Share
493 | 2005-07-27 | 123 | E-MIO | METC | Tallmadge Remove Reactors | Tallmadge Remove Reactors | MI |  |  | Emergency overload of either Tallmadge transformer for the outage of the other Tallmadge transformer with Cobb 5 in 2007 (102%). Part of third Tallmadge transformer project. (PrjID 481) | [20 empty] | Y |  |  | Not Shared
494 | 2005-07-27 | 58 | E-MIO | METC | Battle Creek - Verona 138kV #1 Line | Remove Sag Limit | MI |  |  |  |  | Budgeted | Not Required |  | 0% | [15 empty] | Y |  |  | Excluded
642 | 2005-07-27 | 57 | E-MIO | METC | Argenta - Hazelwood(Sag) 138 ckt # 1 | Argenta - Hazelwood(Sag) 138 ckt # 1 | MI |  |  |  |  | Approved | Not Required |  | 0% | [15 empty] | Y |  |  | Excluded
643 | 2005-07-27 | 60 | E-MIO | METC | Gaines - Thompson Road 138 ckt # 1 | Gaines - Thompson Road 138 ckt # 1 | MI |  |  |  |  | Approved | Not Required |  | 5% |  |  | METC_2011Sum_U7-28-2005_29.idv | [12 empty] | Y |  |  | Excluded
644 | 2005-07-27 | 64 | E-MIO | METC | Rogue River 138 ckt # 1 | Rogue River 138 ckt # 1 | MI |  |  | Customer connection (distribution interconnection) |  | Approved | Not Required |  | 0% | [12 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
645 | 2005-07-27 | 56 | E-MIO | METC | American Bumper - David 138 ckt # 1 | Rebuild line to 795 ACSS | MI |  |  | Contingency Overload of 336 ACSR for Goss 345/138 kV Transformer Out (109%). Normal condition overload in 2008. |  | Budgeted | Not Required |  | 0% | [15 empty] | Y |  |  | Not Shared
646 | 2005-07-27 | 86 | E-MIO | METC | Edenville - Warren 138 ckt # 1 | Rebuild Edenville-Warren 138 kV line 14.75 miles to 795 ACSS | MI |  |  | Normal Overload of 266 ACSR for the Gallagher Transformer Bank Out in 2010 (103%). |  | Budgeted | Not Required |  | 0% | [15 empty] | Y |  |  | Not Shared
648 | 2005-07-27 | 75 | E-MIO | METC | Various Distribution Connections 138 ckt # 1 | Various Distribution Connections 138 ckt # 1 | MI |  |  | Distribution interconnections in 2007 |  | Budgeted | Not Required |  | 0% | [15 empty] | Y |  |  | Not Shared
649 | 2005-07-27 | 81 | E-MIO | METC | Argenta - Palisades(Sag) 345 ckt # 1&2 | Argenta - Palisades(Sag) 345 ckt # 1&2 | MI |  |  | Outage of one of the Argenta - Palisades 345kv ckts exceeds the sag limit rating of the other. |  | Not Budgeted | Not Required |  | 0% | [15 empty] | Y
650 | 2005-07-27 | 72 | E-MIO | METC | Battle Creek - Morrow 138 ckt # 1 | Rebuild Battle Creek-Morrow 138 kV line 14.4 miles to 795 ACSS | MI |  |  | Contingency Overload of the 6-wired 4/O ACSR with 2/O Cu for the Argenta to Battle Creek and the Argenta to Tompkins 345 kV Tower Line Out (101% in 2010) Also a poor performing circuit. |  | Budgeted | Not Required |  | 0% | [15 empty] | Y |  |  | Not Shared
651 | 2005-07-27 | 83 | E-MIO | METC | Stover - Clearwater 138 kV Line (Phase 2) | Rebuild Stover - Clearwater 138 kV line 8.8 miles to 795 ACSS | MI |  |  | Phase 2 of Project 660. Contingency Overload of 266 ACSR for Keystone to Livingston 345 kV Line Out with Karn 4 Off (106%) |  | Budgeted | Not Required |  | 0% | [15 empty] | Y |  |  | Not Shared
653 | 2005-07-27 | 88 | E-MIO | METC | Various Distribution Connections 138 ckt # 1 | Various Distribution Connections 138 ckt # 1 | MI |  |  | Distribution interconnections in 2008 |  | Budgeted | Not Required |  | 0% | [15 empty] | Y |  |  | Not Shared
654 | 2005-07-27 | 84 | E-MIO | METC | Almeda - Saginaw River 138 ckt # 1 | Rebuild Almeda - Saginaw River 138 kV line 25 miles to 795 ACSS | MI |  |  | Contingency Overload of the 1/O, 110, and 115 Cu for Livingston Gallagher Tittabawassee 345 kV Line Out with Campbell 3 Off (114%) |  | Not Budgeted | Not Required |  | 0% | [15 empty] | Y |  |  | Share
658 | 2005-07-27 | 82 | E-MIO | METC | Gaylord - Livingston 138 ckt # 1 | Reconductor 1.5 miles to 795 ACSS | MI |  |  | Normal Overload for Gallagher 345/138 kV Transformer Out (105%) |  | Not Budgeted | Not Required |  | 0% | [15 empty] | Y |  |  | Not Shared
660 | 2005-07-27 | 101 | E-MIO | METC | Keystone - Clearwater - Stover 138 kV line Phase 1 | Rebuild 23.2 miles to 795 ACSS, Keystone to Clearwater | MI |  |  | Contingency Overload of 266 ACSR for Keystone to Livingston 345 kV Line Out with Karn 4 Off (106%) |  | Budgeted | Not Required |  | 0% | [6 empty] | Stover - Clearwater is Project 651 | [8 empty] | Y |  |  | Share
662 | 2005-07-27 | 117 | E-MIO | METC | Weeds Lake 345/138 kV Station | Construct new 345/138 kV single transformer station | MI |  |  | Normal loading of the Argenta 345/138 kV transformers for the loss of either of the remaining two Argenta transformers. |  | Not Budgeted | Not Required |  | 0% | [15 empty] | Y
663 | 2005-07-27 | 105 | E-MIO | METC | Various Distribution Connections 138 ckt # 1 | Various Distribution Connections 138 ckt # 1 | MI |  |  | Customer Connections (distribution interconnections) in 2009 |  | Budgeted | Not Required |  | 0% | [15 empty] | Y |  |  | Not Shared
740 | 2006-07-05 | 41, 44, 45, 46 | East | METC | 345 kV line relaying and communications upgrade project - Phase 1 | Phase 1 Upgrade 345 kV line relaying and communications on Gallagher - Tittabawassee, Keystone - Livingston, and Livingston - Gallagher lines. | MI |  |  |  |  | Approved | Not Required | [8 empty] | 99104 | METC - Russ Vente |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
741 | 2005-07-27 | 68, 69, 70, 71 | E-MIO | METC | 345 kV line relaying and communications upgrade project - Phase 2 | Phase 2 Upgrade 345 kV line relaying and communications on Argenta - Battle Creek, Argenta - Tompkins and Battle Creek - Onedia lines. | MI |  |  |  |  | Budgeted | Not Required |  | 0% | [6 empty] | 99105 | [8 empty] | Y |  |  | Excluded
742 | 2005-07-27 | 77, 78, 79, 80 | E-MIO | METC | 345 kV line relaying and communications upgrade project - Phase 3 | Phase 3 Upgrade 345 kV line relaying and communications on Goss - Thetford, Nelson Road - Kenowa, and Nelson Road - Goss liens. | MI |  |  | Relay upgrades |  | Budgeted | Not Required |  | 0% | [6 empty] | 99106 | [8 empty] | Y |  |  | Share
743 | 2005-07-27 | 90, 91, 92, 93, 94, 95 | E-MIO | METC | 345 kV line relaying and communications upgrade project - Phase 4 | Phase 4 Upgrade 345 kV line relaying and communications on Hampton - Thetford # 1, Hampton - Thetford #2, Hampton - Tittabawassee, Thetford - Tittabawassee, Tittabawassee - Nelson Road lines | MI |  |  | Relay upgrades |  | Budgeted | Not Required |  | 0% | [6 empty] | 99107 | [8 empty] | Y |  |  | Share
744 | 2005-07-27 | 106, 107, 108, 109, 110, 111 | E-MIO | METC | 345 kV line relaying and communications upgrade project - Phase 5 | Phase 5 Upgrade 345 kV line relaying and communications on Argenta - Tallmadge, Campbell - Tallmadge, Ludington - Tallmadge, Tallmadge - Kenowa, Tallmadge - Roosevelt lines | MI |  |  | Relay upgrades |  | Budgeted | Not Required |  | 0% | [6 empty] | 99108 | [8 empty] | Y |  |  | Share
772 | 2006-07-05 | 66 | East | METC | Tallmadge 345 kV Transformer Bushing Replacements TBD | Tallmadge 345 kV Transformer Bushing Replacements TBD | MI |  |  |  |  | Budgeted | Not Required | [9 empty] | METC - Russ Vente |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
773 | 2005-07-27 | 47 | E-MIO | METC | Tittabawassee & Kenoa 345 kV Breaker Replacements 3000 Amp | Tittabawassee & Kenoa 345 kV Breaker Replacements 3000 Amp | MI |  |  |  |  | Approved | Not Required |  | 50% | [12 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
774 | 2005-07-27 | 61 | E-MIO | METC | Gaylord 138 kV 36 MVAR Capacitors | Gaylord 138 kV 36 MVAR Capacitors | MI |  |  |  |  | Approved | Not Required |  | 0% | [15 empty] | Y |  |  | Excluded
775 | 2005-07-27 | 62 | E-MIO | METC | Iosco 138 kV 18 MVAR Capacitors | Iosco 138 kV 18 MVAR Capacitors | MI |  |  |  |  | Budgeted | Not Required |  | 0% | [15 empty] | Y |  |  | Excluded
776 | 2005-07-27 | 76 | E-MIO | METC | Various 138 kV 72 MVAR Capacitors | Various 138 kV 72 MVAR Capacitors | MI |  |  | To solve normal and contingency voltage problems. |  | Budgeted | Not Required |  | 0% | [15 empty] | Y |  |  | Not Shared
777 | 2005-07-27 | 89 | E-MIO | METC | Various 138 kV 72 MVAR Capacitors | Various 138 kV 72 MVAR Capacitors | MI |  |  | To solve normal and contingency voltage problems. |  | Budgeted | Not Required |  | 0% | [15 empty] | Y |  |  | Not Shared
976 | 2005-07-27 | 48 | E-MIO | METC | Alpine - Add one line switch | Install a tap pole and one switch on Four Mile-N Belding 138kV line | MI | [10 empty] | METC_2011Sum_U7-28-2005_29.idv | [6 empty] | 2005-07-27 | [5 empty] | Y |  |  | Not Shared
977 | 2005-07-27 | 49 | E-MIO | METC | Marquette 138 kV station | Replace breaker failure scheme | MI | [17 empty] | 2005-07-27 | [5 empty] | Y |  |  | Not Shared
980 | 2005-07-27 | 59 | E-MIO | METC | Arthur | Install a tap pole and one two-way switch on Cobb - Tallmadge #2 138kV Line | MI | [10 empty] | METC_2011Sum_U7-28-2005_29.idv | [6 empty] | 2005-07-27 | [5 empty] | Y |  |  | Not Shared
981 | 2005-07-27 | 63 | E-MIO | METC | Wabasis | Install a tap pole and two switches on N. Belding - Vergennes 138kV Line | MI | [10 empty] | METC_2011Sum_U7-28-2005_29.idv | [6 empty] | 2005-07-27 | [5 empty] | Y |  |  | Not Shared
982 | 2005-07-27 | 65 | E-MIO | METC | Crahen | Install a tap pole and one switch on Spaulding-Race St.-Four Mile 138kV line | MI | [10 empty] | METC_2011Sum_U7-28-2005_29.idv | [6 empty] | 2005-07-27 | [5 empty] | Y |  |  | Not Shared
983 | 2005-07-27 | 113 | E-MIO | METC | 345 kV line relaying and communications upgrade project - Phase 6 | Phase 6 upgrade 345 kV line relaying and communications | MI |  |  | Relay upgrades | [14 empty] | 2005-07-27 | [5 empty] | Y |  |  | Share
984 | 2005-07-27 | 114 | E-MIO | METC | Denver 345/138 kV station | Build new 345/138 kV station, 50 miles 345 kV line, 60 miles 138 kV lines | MI |  |  | Contingency Overload of Tittabawassee TB2 for Tittabawassee TB1 out (107%) Contingency overload of 30 mile Tippy to chase 138 kV line for Croton to Nineteen Mile 138 kV line (114%). Also low voltage at Mecosta Area, Midland (Summerton) Area,and Clare (Warren) Area | [14 empty] | 2005-07-27 | [5 empty] | Y |  |  | Share
985 | 2005-07-27 | 115 | E-MIO | METC | 345 kV line relaying and communications upgrade project - Phase 7 | Phase 7 upgrade 345 kV line relaying and communications | MI |  |  | Relay upgrades | [14 empty] | 2005-07-27 | [5 empty] | Y |  |  | Share
986 | 2005-07-27 | 116 | E-MIO | METC | 345 kV line relaying and communications upgrade project - Phase 8 | Phase 8 upgrade 345 kV line relaying and communications | MI |  |  | Relay upgrades | [14 empty] | 2005-07-27 | [5 empty] | Y
987 | 2005-07-27 | 118 | E-MIO | METC | Emmet - Stover 138 kV Line | Build 30 miles new 138 kV line, 795 ACSS | MI |  |  | Contingency Voltage less than 0.92 pu for Emmet to Livingston 138 kV line | [14 empty] | 2005-07-27 | [5 empty] | Y
988 | 2005-07-27 | 120 | E-MIO | METC | Simpson - Batavia 138 kV line | Build 30 miles new 138 kV line, 795 ACSS | MI |  |  | Normal Overload of 266 ACSR for Project 1(?) generation out in 2008 (102%). | [11 empty] | MISO Project 1 is not gen. What gen is Project 1? |  |  | 2005-07-27 | [5 empty] | Y |  |  | Share
991 | 2005-07-27 | 127 | E-MIO | METC | Argentine - CE Lovejoy | Argentine - (NDS) - No METC Facility | MI | [10 empty] | METC_2011Sum_U7-28-2005_29.idv | [6 empty] | 2005-07-27 | [5 empty] | Y
1014 | 2005-08-12 | 130 | E-MIO | METC | Oakland | Oakland - Capacitors Increase | MI | [10 empty] | METC_2011Sum_U2_8-12-2005_29.idv | [6 empty] | 2005-08-12 | [5 empty] | Y |  |  | Not Shared
1015 | 2005-08-12 | 131 | E-MIO | METC | Oden | Oden - New Capacitor | MI | [17 empty] | 2005-08-12 | [5 empty] | Y |  |  | Not Shared
1016 | 2005-08-12 | 132 | E-MIO | METC | Bard Road | Bard Road - New Capacitor | MI |  |  | Low voltage for loss of the Gallagher 345/138 kV transformer | [14 empty] | 2005-08-12 | [5 empty] | Y |  |  | Not Shared
1017 | 2005-08-12 | 133 | E-MIO | METC | Croton | Croton - New Capacitor | MI |  |  | Low voltage for loss of Four Mile - Piston Ring 138 kV ckt. | [14 empty] | 2005-08-12 | [5 empty] | Y |  |  | Not Shared
1225 | 2005-11-28 | 98 | E-MIO | METC | Thompson Rd-Tallman 138 kV | Thompson Road - Tallman 138 kV line | MI |  |  | Overload caused by outage of David-Bingham 138 kV ckt 1 | [20 empty] | Y
98 | 2006-03-24 |  | N-NM | MH | Ridgeway - Selkirk 230 line and Selkirk 230/115 transformer | Ridgeway - Selkirk 230 line and Selkirk 230/115 transformer | Manitoba |  |  |  |  | Budgeted | Pending | [9 empty] | MH - David Diakiw |  |  |  |  | 2003-06-25 |  |  | Y
264 | 2006-03-24 | 264 | N-NM | MH | Wuskwatim Generation Outlet Transmission Facilities | New outlet transmission facilities required for a new 200 MW generating plant being built near Thompson, Manitoba. This project includes Birchtree - Wuskwatim 230 line, Herblet Lake - Wuskwatim 230 line, 2 Herblet Lake - Wuskwatim 230 lines, & a Thompson Birchtree 150/-20 MVAR SVC. | Manitoba |  |  | New Generation | Wuskwatim Generation Outlet Transmission Facilitie MTEP06.doc | Budgeted | Obtained | Low | 0% | [7 empty] | MH - David Diakiw |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Not Shared
278 | 2006-03-24 |  | N-NM | MH | Dorsey - Portage South 230 ckt 2 | Dorsey - Portage South 230 ckt 2, Sum rate 384 | Manitoba |  |  |  |  | Budgeted | Required | [9 empty] | MH - David Diakiw | [7 empty] | Y
283 | 2006-03-24 | 283 | N-NM | MH | New Rosser Oak Point Station 115-24 kV | A new Rosser - Oak Point station is going to be built to supply area load growth. The project consists of two new 115/24 kV transformers, plus associated station equipment and 24 kV feeders. This station will be tapped of of existing 115 kV lines RY7 and RK6. | Manitoba |  |  | Future Load Growth | New Rosser Oak Point Station 115-24 kV MTEP06.doc | Budgeted | Pending | Low | 0% | [7 empty] | MH - David Diakiw | [7 empty] | Y
285 | 2006-06-28 |  | N-NM | MH | St. Vital - Steinbach 230 | St. Vital - Steinbach 230 ckt 1, Sum rate 399 | Manitoba |  |  |  |  | Budgeted | Required |  |  | a second 230-66 kV transformer bank at Richer, which is planned to be in-service in 2007 | [6 empty] | MH - David Diakiw | Deferred by Alternative for 2007 Project is changed from planned to proposed as it was deferred to 2020. Higher load growth in the Steinbach area required a new plan. This plan consists of a second 230-66 kV transformer bank at Richer, which is planned to be in-service in 2007. The second bank provides for immediate load serving needs and defers the need for the 230 kV line. The budget for the alternative transformer bank has been approved and design is underway. |  |  |  | 2005-06-16 |  |  | Y
288 | 2006-03-24 | 288 | N-NM | MH | Dorsey to Forbes 500 kV Line Sectionalization (D602F) | This is a new 230 kV station wich will sectionalize the existing 500 kV line D602F into the station as well as several existing 230 kV lines. This station will also have a new 500/230 kV transformer installed. | Manitoba |  |  | New D.C line (bipole 3 from North) | Dorsey to Forbes 500 kV Line Sectionalization (D602F) MTEP06.doc | Budgeted | Pending | Low | 0% | [7 empty] | MH - David Diakiw | [7 empty] | Y |  |  | Not Shared
289 | 2006-06-28 |  | N-NM | MH | Henday - Riel 500 dc | Henday - Riel 500 dc ckt 1, Sum rate 2000 | Manitoba |  |  |  |  | Budgeted | Required | [9 empty] | MH - David Diakiw | [7 empty] | Y
291 | 2006-03-24 | 291 | N-NM | MH | Great Falls & Pine Falls-Bloodvein Improvements | Replacement lines and equipment to existing 66 kV and upgrade to 115 kV supplies | Manitoba |  |  | Load growth and reliability | Great Falls & Pine Falls-Bloodvein Improvements MTEP06.doc | Budgeted | Pending | Low | 0% | [7 empty] | MH - David Diakiw | [7 empty] | Y |  |  | Not Shared
442 | 2006-03-24 | 442 | N-NM | MH | Winnipeg to Brandon Transmission System Improvements | addition of three Portage South station 10 MVAR 66 kV capacitors and 1 Brandon 115, 54 MVAR Capacitor | Manitoba |  |  | voltage reliability |  | Budgeted | Pending | Low | 0% | [7 empty] | MH - David Diakiw |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Not Shared
557 | 2005-07-11 | 557 | N-NM | MH | West Kildonan - Court 115 - 7.2 kV Bank Addition | Court transformer #2 (companion bank) tapped off of line RL2 | Manitoba |  |  | Load growth |  | Pending | Obtained | Low | 0% | [6 empty] | $4,571,912 | [8 empty] | Y
604 | 2006-03-24 | 604 | N-NM | MH | Flin Flon Area Transmission Improvements Phase II | Transmission: Design and construct 6 km of single circuit, 115 kV line between Herblet Lake station and Chisel Lake disconnect switch 1521. Upgrade 73 km of HS15 between Herblet Lake and Sherridon Station. Fix towers and insulators where required and clean up right of way. Salvage 65 km of 115 kV line HS15 between I1F/12F tap and Sherridon station. At Herblet Station, build a wood pole 115 kV line and provide a provision for temporarily connecting H59C to the 115 kV line HS15. At Cliff Lake station build a wood pole 115 kV line and provide a provision for temporarily connecting bank 3 secondary to line H59C Station: De-commission and salvage the Mile 13 station. Salvage 230-115-13.8 kV 30/40/45 MVA station service transformer at Ponton station. Relocate Ponton 30/40/45 MVA transformer bank to Herblet Lake station. Co-terminate the transformer on the 230 kV side and add one 115 kV breaker and associated equipment. At Cliff Lake station install/modify bank 3 protection equipment as required. Increase the capacity of communication diesel generating facilities and use as the permanent back-up local service supply for Ponton station. | Manitoba |  |  | Facilities are required to decommission crumbling Mile 13 Station and Switch Tower #3, to enhance reliability of transmission to HBM&S, to firm transformation at Herblet Lake Station, and to firm supply to Snow Lake area loads. | Flin Flon Area Transmission Improvements Phase II MTEP06.doc | Budgeted | Pending | Low | 0% | Alternative to the 115 kV line from Herblet Lake to the Chisel Lake tap to provide a dedicated supply to Sherridon: 1. Supply Sherridon station via new 25 kV distribution facilities from Snow Lake station. This option was rejected because it would have resulted in longer outages and allowed for no load growth at Sherridon. Alternatives to the relocation of the Ponton 50 MVA, 230 – 115 kV transformer to Herblet Lake station: 1. Purchase and install a new 230 – 115 kV transformer at Herblet Lake station. 2. Relocate Cliff Lake Bank 3 to Herblet Lake station. Alternative to the Ponton station service equipment: 1. Purchase and install a new 230 kV – 120 V power voltage transformer a Ponton station. All of the above alternatives were not pursued because they would have resulted in increased complexity and cost. | [6 empty] | MH - David Diakiw | Cliff Lake, Herblet Lake T/L Improvements 2002 10 31 Ponton Salvage & Herblet Bank installation 2003 10 31 Salvage Mile 13 2007 03 30 HS15 T/L Upgrade and Salvage 2007 03 30 Herblet Lake -Chisel Lake Tap 2007 03 30 |  |  |  | 2005-06-16 |  |  | Y |  |  | Not Shared
912 | 2006-06-28 | 2 | N-NM | MH | Point du Bois Generating Station Rehabilitation/Redevelopment | Point du Bois - Rover 115 kV new line will replace aging existing two 66 kV lines | Manitoba |  |  | New Generation | Point du Bois Generating Station Rehabilitation/Redevelopment MTEP06.doc | Pending | Required | low | 0% | [6 empty] | $24,803,532 |  |  | 2005-07-11 | [5 empty] | Y |  |  | Not Shared
913 | 2006-06-28 | 3 | N-NM | MH | Richer South 230-66 kV Transformer Addition | Addition of a of a second Richer South 230-63.5 kV, Sum rate 93 MVA transformer is to be installed. | Manitoba |  |  | load growth | Richer South 230-66 kV Transformer Addition MTEP06.doc | Pending | Required | low | 0% | [6 empty] | $7,251,831.03 |  |  | 2005-07-11 | [5 empty] | Y
914 | 2006-06-28 | 4 | N-NM | MH | Ridgeway 230-66 kV Transformer Addition | Addition of a third 230-63.5 kV, Sum rate 140 MVA Ridgeway transformer | Manitoba |  |  | load growth | Ridgeway 230-66 kV Transformer Addition MTEP06.doc | Pending | Required |  | 0% | [6 empty] | $7,468,772.91 |  |  | 2005-07-11 | [5 empty] | Y
915 | 2006-06-28 | 5 | N-NM | MH | Selkirk Area Improvements | This project consists of a new 230 kV line from Rosser to Parkdale and development of a new 230/110 kV station to replace the existing Parkdale station. Rosser 230-115 kV Transformer Upgrade, 176 to 250 MVA | Manitoba |  |  | load growth |  |  | Required | [8 empty] | $2,464,590.26 |  |  | 2005-07-11 | [5 empty] | Y |  |  | Not Shared
917 | 2006-06-28 | 7 | N-NM | MH | Southwest Winnipeg Transmission Improvements | re-conductor of section of St Vital -LaVerendrye(YV5) 115 to increase Sum rate to 178.9 MVA and reconfigure lines VH2 & XS49 | Manitoba |  |  | reliability and load growth |  | Pending | Required | low | 0% | [6 empty] | $484,464 |  |  | 2005-07-11 | [5 empty] | Y |  |  | Not Shared
1013 | 2006-06-28 | 1 | N-NM | MH | Neepawa 230 - 66 kV Station | A new 230/66 kV station is to be built which will include sectionalizing Line D54C into the station, a 230/66kV, 90 MVA transformer & new 230 and 66 kV ring busses | Manitoba |  |  | load growth | Neepawa 230 - 66 kV Station MTEP06.doc | Pending | Required | low | 0% | [6 empty] | $16,462,591.95 |  |  | 2005-07-11 | [5 empty] | Y |  |  | Not Shared
277 | 2005-06-15 | 272 | N-NM | MP | Badoura Project | Badoura - Pequot Lakes 115 ckt 1, Sum rate 182 | MN |  |  |  |  | Approved | Pending | [17 empty] | Y |  |  | Share
1021 | 2005-08-29 |  | N-NM | MP/GRE | Embararss to Tower 115 kV Line | 115 kV line from 34L tap to Tower 46 kV | MN |  |  | post-contingent voltage support and loading on 46 kV | [5 empty] | generation or 46 kV line | [8 empty] | 2005-08-29 | [5 empty] | Y |  |  | Share
1022 | 2005-08-29 |  | N-NM | MP/GRE | Badoura-Long Lake 115 kV line | 115 kV line from MP Badoura to GRE Long Lake | MN |  |  | post-contingent voltage support and line loading | [5 empty] | Akeley to Long Lake | [8 empty] | 2005-08-29 | [5 empty] | Y |  |  | Share
279 | 2005-07-29 | 274 | N-NM | MPC/XEL/OTP/MP | Boswell - Wilton 230 kV Line | Boswell - Wilton 230 ckt 1, Sum rate 390 | MN |  |  | Winter Peak conditions with heavy transfers north to Manitoba are showing some voltage stability concerns in the Red River Valley - This project will help alleviate these concerns | Red River Valley / West Central Minnesota Transmission Improvement Planning Study (RRV/WMN TIPS) | Pending | Pending | Low | 0% | Coal Creek - Underwood - Harvey - Prairie 345 kV Line; Garrison - Max - Minot - Rugby - Drayton 230 kV Line; Bismarck - Jamestown - Fargo 345 kV Line; Boswell - Wilton 230 kV Line; Dorsey - Karlstad - Winger 345 kV Line; Fargo - Moorhead - Morris - Granite Falls - Blue Lake 345 kV Line; Watertown - Granite Falls - Blue Lake 345 kV Line | [14 empty] | Y |  |  | Share
612 | 2006-06-30 | 9325101 | E-MIO | NIPS | Hiple - Add 2nd 345-138 kV Transformer | Install a 2nd 345/138 kV 560 MVA transformer, associated breakers and bus at F.G. Hiple Substation. | IN |  |  | Double contingencies involving loss of existing Hiple 345/138 kV transformer and other local 138 kV circuits results in 138 kV circuit overloading and low voltage levels on the local 138 kV and 69 kV systems. | [20 empty] | Y |  |  | Not Shared
757 | 2006-06-30 | 9320027 | E-MIO | NIPS | Dune Acres - Add 138 kV Capacitors - 100 MVAR | Add one step of capacitors, for a total 100 MVAR, on the Dune Acres 138 kV bus. | IN |  |  | Additional capacitors will supply internal reactive needs and provide voltage support to 138 kV industrial customers throughout the year under various system conditions. |  | Budgeted | Not Required | [14 empty] | 2005-06-16 |  |  | Y |  |  | Excluded
919 | 2006-06-30 | 9320020 | E-MIO | NIPS | Lagrange - Increase #1 138-69KV Transformer Capacity to 168 MVA | Replace Lagrange #1 138/69 kV 112 MVA transformer with a 168 MVA transformer. | IN |  |  | Loss of single station transformer causes the remaining unit to overload in 2008. | [14 empty] | 2005-07-08 | [5 empty] | Y
920 | 2006-06-30 | 71C6113 | E-MIO | NIPS | Hiple - Add 2nd 138-69 KV 112 MVA Transformer | Install a 2nd 138/69 KV 112 MVA transformer, associated breakers and bus at Hiple Substation. | IN |  |  | Loss of local 69 kV circuit results in a transformer load of 105% of rating in 2005. | [14 empty] | 2005-07-08 | [5 empty] | Y
921 | 2006-06-30 | 71C6307 | E-MIO | NIPS | Goodland - Replace #1 & 2 Transformers - Increase Capacity to 112 MVA ea. | Upgrade existing two 138/69 kV transformers, associated switches, buses, breakers, etc. to accommodate two 138/69 kV 112 MVA transformers. | IN |  |  | Loss of single station transformer causes the remaining unit to overload in 2005. | [14 empty] | 2005-07-08 | [5 empty] | Y
922 | 2006-06-30 | 71C6331 | E-MIO | NIPS | Michigan City to Luchtman Rd -Upgrade Capacity | Increase circuit capacity between Michigan City Gen. Station and Luchtman Road (5 mi.). Upgrade to 954 KCM ACSR and 316 MVA rating. | IN |  |  | Loss of Flint Lake - Tower Road Circuit results in a circuit load of 105% of rating in 2005. | [14 empty] | 2005-07-08 | [5 empty] | Y |  |  | Not Shared
923 | 2006-06-30 | 71C6602 | E-MIO | NIPS | Plymouth - Add 3rd 138-69KV 168 MVA Transformer | Install a 3rd 138/69 KV 168 MVA transformer, associated breakers and bus at Plymouth to increase station capacity. | IN |  |  | Loss of single station transformer causes the remaining unit to overload by 101% in 2005. | [14 empty] | 2005-07-08 | [5 empty] | Y
925 | 2006-06-30 | 71C6613 | E-MIO | NIPS | ISG2 to Marktown - Upgrade Capacity | Upgrade circuit capacity on existing .6 miles of 300 KCM Cu line by bundling both sets of 300 KCM CU line on shared tower line between Marktown and ISG #2 to increase capacity to 316 MVA. | IN |  |  | Loss of WCE - Marktown East results in a circuit load of 112% of rating in 2005. | [14 empty] | 2005-07-08 | [5 empty] | Y |  |  | Not Shared
926 | 2006-06-30 | 9325540 | E-MIO | NIPS | Monticello - Add 69 kV Capacitors - (4) Stages 10.8 MVAR | Add four steps capacitors of 10.8 MVAR each, for a total 43.2 MVAR, on the Monticello Sub 69 kV bus. | IN |  |  | Additional capacitors will supply internal reactive needs and provide local voltage support. | [14 empty] | 2005-07-08 | [5 empty] | Y
1113 | 2005-11-18 | G162 |  | NSP | G162, 37228-01 | Net: A new Fenton 115 KV substation to be built on the Chanarambie – Nobles 115 KV transmission line. A restudy will be done if the associted facilties shown below are not met: For the 425 MW wind generations upgrade -115 KV from Chanarambie to Ellsborough to Yankton, Second Ckt from Lk Yankton to Leon , Lk. Yankton 115 KV, +/- 60 MVAR; Plus cap banks 4*20, 40, 2*20 MVA For 825 MW wind generations upgrade -New Chanarambie – Fenton – Nobles 115 KV transmission line, new Buffalo Ridge – White 115 KV transmission line, new Split Rock – Lk. Field Junction 345 KV transmission line, Lake Field Junction – Fox Lake 161 KV line. Int: Install a 200 MW wind farm generating facility in or near Nobles County, MN. | MN |  |  | http://www.midwestiso.org/plan_inter/documents/generation_inter/G162_IES_Report.zip | [13 empty] | http://www.midwestiso.org/plan_inter/documents/generation_inter/G162_FacilityStudy.zip | 2001-12-03 | [5 empty] | Y | 2006-05-01
1117 | 2005-11-18 | G170 |  | NSP | G170, 37272-01 | Net: None. Int: Increase the output of an existing 571 MW facility located at the A.S. King plant, by 20 MW net, for a total output of 591 MW net. | MN |  |  | http://www.midwestiso.org/plan_inter/documents/generation_inter/G170_Deliverability_Study_Report.pdf | [13 empty] | www.midwestiso.org/plan_inter/documents/G170_R3_Report.pdfhttp://www.midwestiso.org/plan_inter/documents/G170_R3_Report.pdf | 2002-01-16 | [5 empty] | Y | 2008-01-01
1118 | 2005-11-18 | G173 |  | NSP | G173, 37305-01 Faribault Energy Center | Net: None. Int: A 300 MW electric generating facility located in Rice County, Minnesota. A new 115kV substation configuration will consist of a three-position ring bus. There will be three elements in the ring: the 115kV interconnect for the Facility, the 115kV West Faribault line, and the 115kV Lake Marion line. 1.4.3 Re-conductor 115kV transmission line 0832 from FEP to Lake Marion substation,1.4.4 Install 795kcmil 26/7 ACSS conductor on 115kV H-frame structures (about 19 miles, re-conductor 115kV transmission line 0832 from FEP to West Faribault substation, install 795kcmil 26/7 ACSS conductor on 115kV H-frame structures (about 5.5 miles), rebuild 69kv Line Number 0705 from Fair Park Sub to Northfield Substation, install 477 kcmil 26/7 ACSS conductor on 69kV horizontal post structures (about 13 miles). | MN |  |  | http://www.midwestiso.org/plan_inter/documents/G173_r2_report.pdf | [13 empty] | http://www.midwestiso.org/plan_inter/documents/G173_Facilities_Study.pdf | 2002-02-18 | [5 empty] | Y | 2004-04-01
1120 | 2005-11-18 | G185 |  | NSP | G185, 37336-01 | Net: Break the existing 69 KV line 0727 to provide a tap connection.. Int: Install a 4.5 MW wind farm. | MN |  |  | http://www.midwestiso.org/plan_inter/documents/G185_IES_Report.zip | [13 empty] | http://www.midwestiso.org/plan_inter/documents/generation_inter/G185_FacilityStudy.zip | 2002-03-21 | [5 empty] | Y | 2006-06-30
1127 | 2005-11-18 | G239 |  | NSP | G239, 37432-01 | Net: Install a 2nd 34.5/69 kV transformer, 69 kV circuit breaker, 34.5 kV circuit breaker and associated protection equipment. Int: 22.5 MW gross MW net wind generating units located in Dodge Center, Minnesota. | MN |  |  | http://www.midwestiso.org/plan_inter/documents/G239_R2_report.zip | [13 empty] | http://www.midwestiso.org/plan_inter/documents/generation_inter/G239_IFS_Report.pdf | 2002-06-25 | [5 empty] | Y | 2002-09-01
1138 | 2005-11-18 | G261 |  | NSP | G261, 37540-02 | Net: For Phase 1-Transmission design and install one 115 KV line from Mankato Energy Park substation to the Wilmarth Substation.Transmission Design and Install one 345 KV line from the Mankato Energy Park to the Wilmarth 345 KV substation. For Phase 2-Stringing of second 115 KV line from Wilmarth substation to Mankato Energy Park substation; reterminate Sumit line and deferral costs. Int: Construct a 667 MW summer net two-on-one combined cycle generating facility with its electrical equipment, including three generator step up transformers, one 345 kV breaker, two 115 kV breakers, and all associated protection and metering equipment. | MN |  |  | http://www.midwestiso.org/plan_inter/documents/generation_inter/G261_IES_Report.zip | [13 empty] | http://www.midwestiso.org/plan_inter/documents/generation_inter/G261_IFS_report.pdf | 2002-10-11 | [5 empty] | Y | 2007-05-01
1145 | 2005-11-18 | G237 |  | NSP | G237, 37642-01 | Net: One half of the bifurcated line to Rogers Lake will be rebuilt and the entire 8.5 mile 115 kV line will be reconductored with 795 kcmil ACSS phase conductors and 110.8 kcmil ACSR shield wire. Int: Increase the output of an existing 262 MW net generating facility located at the Highbridge plant, by 313 MW net, for a total output of 575 MW net. | MN |  |  | http://www.midwestiso.org/plan_inter/documents/generation_inter/G237_IES_Report.zip | [13 empty] | http://www.midwestiso.org/plan_inter/documents/generation_inter/G237 Highbride Power Plant Facility Studies.pdf | 2003-01-21 | [5 empty] | Y | 2008-05-01
274 | 2005-07-29 | 269 | N-NM | OTP | Appleton - Dawson 115 kV Line | Appleton - Dawson 115 ckt 1, Sum rate 96 | MN |  |  | Increasing load at Dawson is causing loading concerns on Canby 115/41.6 kV transformer - Project will move load to the 115 kV system | [20 empty] | Y |  |  | Not Shared
275 | 2005-07-29 | 270 | N-NM | OTP | Canby - Dawson 115 kV Line | Dawson - Canby 115 ckt 1, Sum rate 96 | MN |  |  | Increasing load at Dawson is causing loading concerns on Canby 115/41.6 kV transformer - Project will move load to the 115 kV system | [20 empty] | Y |  |  | Not Shared
549 | 2005-07-29 | p2-108 | N-NM | OTP | Jamestown Reactor Addition | Jamestown 115 kV 25 MVAR reactor | ND |  |  | Outage of Buffalo - Maple River 345 kV line results in high voltage issues around Jamestown 115 kV system | [8 empty] | 436672 | [11 empty] | Y |  |  | Not Shared
585 | 2006-03-27 | 585 | N-NM | OTP | Pelican Rapids 115 kV Line Uprate | Pelican Rapids - Pelican Rapids Turkey Plant 115 kV line | MN |  |  | Loading concerns on 41.6 kV system during contingencies on sub-transmission system are evident - Moving load to 115 kV will prolong life of 41.6 kV system |  | Pending | Pending | [9 empty] | OTP - Jason Weiers |  |  |  |  | 2005-06-16 |  |  | Y
973 | 2005-11-01 | G392 | N-NM | OTP | Big Stone II Generation Project | Build New Big Stone - Ortonville 230 kV Line, Convert Ortonville - Johnson Jct. 115 kV line to 230 kV, Convert Johnson Jct. - Morris 115 kV Line to 230 kV, Install a new Johnson Jct. 230/115 kV Transformer, Replace existing Morris 230/115 kV Transforme, Build New Big Stone - Canby 230 kV Line, Convert existing Canby - Granite Falls 115 kV Line to 230 kV, Install a new Canby 230/115 kV Transformer, Upgrade existing Big Stone - Browns Valley 230 kV Line | MN | SD |  | Big Stone II generator interconnection and outlet transmission upgrades. The upgrades are required for interconnection and delivery of Big Stone II generation G392. | Big Stone II Generator Interconnection Report on MISO Generator Interconnection Queue | Pending | Pending | Low | 0% | Big Stone - Willmar 230 kV Line | [8 empty] | 2005-07-29 | [5 empty] | Y |  |  | Share
971 | 2005-07-29 | OTP1 | N-NM | OTP/MPC | Winger 230/115 kV Transformer Upgrade | Winger 230/115 kV Transformer upgrade | MN |  |  | Loss of Winger - Wilton 230 kV line loads up Winger 230/115 kV transformer | Red River Valley / West Central Minnesota Transmission Improvement Planning Study (RRV/WMN TIPS) | Pending | Pending | Low | 0% | Add a 2nd Transformer or replace existing transformer with a larger unit. |  |  | 1475957 | [5 empty] | 2005-07-29 | [5 empty] | Y |  |  | Not Shared
441 | 2005-07-29 | 320 | N-NM | OTP/MRES/GRE | Alexandria Capacitor Addition | Alexandria Poleyard 115 kV, 25 MVAR Capacitors | MN | [23 empty] | Y |  |  | Not Shared
755 | 2005-07-29 |  | N-NM | OTP/MRES/GRE | Alexandria Capacitor Addition | Alexandria Switching Station 115 kV 25 MVAR Capacitors | MN |  |  | Loss of Grant County - Elbow Lake 115 kV line results in low voltage concerns in Alexandria area | [20 empty] | Y |  |  | Not Shared
81 | 2005-06-15 | 57 | C-CSILL | SIPC | Marion Power Plant - Carrier Mills 161 kV line | Construct a 161 kV line connecting the Marion 161 kV Plant to a new Carrier Mills 161/69 kV Substation. The project includes the construction of nearly 27 miles of 161 kV transmission line and converting a 69 kV switching station into a 161/69 kV substation. | IL |  |  | Converting Carrier Mills Switching Station to a 161/69 kV substation appeared to be the best long-term solution for correcting multiple problematic contingencies on the SIPC 69kV network transmission system. The new line and substation will also increase the outlet capacity at the SIPC Marion plant and will be the first stage in networking multiple substations (>100 kV) on the SIPC transmission system. | SIPC_Marion-Carrier Mills 161.doc | Pending | Not Required |  |  | Alternative plans explored, such as rebuilding existing 69 kV lines and building a new 69 kV system tie line, appeared to be only a temporary correction to the problems at hand. | [11 empty] | 2003-06-25 |  |  | Y |  |  | Excluded
182 | 2006-03-16 | 160 | E-IOK | Vectren (SIGE) | Newtonville 161/138 (SIGE) - 161/138 ckt 2 | Newtonville 161/138 (SIGE) - 161/138 ckt 2, Sum rate 168 | IN |  |  | Increase Vectren transfer capability. Contingency Performance. |  | Approved | Not Required | Low | 5% | [7 empty] | Vectren - Fred Fredrick | [7 empty] | Y |  |  | Not Shared
995 | 2006-06-29 |  | E-IOK | Vectren (SIGE) | Add 138/69 kV 60 MVA transformer to Mt. Vernon | Add 138/69 kV 60 MVA transformer to Mt. Vernon | IN |  |  | Contingency performance for Mount Vernon, Indiana area. |  | Budgeted |  | Low |  |  |  |  | 50000 |  |  |  | Vectren - F Fredrick |  | 2005-07-28 | [5 empty] | Y
998 | 2005-07-28 |  | E-IOK | Vectren (SIGE) | Move Newtonville 138/69 kVA 53 MVA transformer to Elliott | Move Newtonville 138/69 kVA 53 MVA transformer to Elliott | IN |  |  | Contingency performance for Evansville, Indiana area. |  |  |  | Low |  |  |  |  | 600000 | [5 empty] | 2005-07-28 | [5 empty] | Y
1001 | 2006-06-29 |  | E-IOK | Vectren (SIGE) | Add 138 kV bus at Oak Grove. Install 150 MVA 138/69 kV transformer | Add 138 kV bus at Oak Grove. Install 150 MVA 138/69 kV transformer | IN |  |  | Contingency performance for Evansville, Indiana area. |  | Budgeted |  | Med |  |  |  |  | 3400000 |  |  |  | Vectren - F Fredrick |  | 2005-07-28 | [5 empty] | Y
1002 | 2006-06-29 |  | E-IOK | Vectren (SIGE) | New Northeast to Oak Grove to Culley Line 138 kV | New Northeast to Oak Grove to Culley Line 138 kV | IN |  |  | Contingency performance for Evansville, Indiana area. |  | Budgeted |  | Med |  |  |  |  | 8500000 |  |  |  | Vectren - F Fredrick |  | 2005-07-28 | [5 empty] | Y |  |  | Share
1004 | 2006-06-29 |  | E-IOK | Vectren (SIGE) | New 345/138 kV Substation at Francisco | New 345/138 kV substation at Francisco | IN |  |  | Increase Vectren transfer capability. Contingency Performance. |  | Budgeted |  | Med |  |  |  |  | 13225000 |  |  | Formerly Snake Run | Vectren - F Fredrick |  | 2005-07-28 | [5 empty] | Y |  |  | Share
1005 | 2006-06-29 |  | E-IOK | Vectren (SIGE) | New 138 kV transmission double circuit Francisco to Northwest/Northeast | New 138 kV transmission double circuit Francisco to Northwest/Northeast Subs with Blue Grass Substation | IN |  |  | Increase Vectren transfer capability. Contingency Performance. |  | Budgeted |  | High |  |  |  |  | 35000000 |  |  | Dependent on Duke approval and obtainment of right-of-way. Formerly Snake Run to Northwest | Vectren - F Fredrick |  | 2005-07-28 | [5 empty] | Y |  |  | Share
1007 | 2006-06-29 |  | E-IOK | Vectren (SIGE) | New 345 kV transmission line Duff to Culley to Smith (OMU) | New 345 kV transmission line Duff to Culley to Smith (OMU) | IN | KY |  | Increase Vectren transfer capability. Contingency Performance. |  | Budgeted |  | High |  | Project 1006: New 345 kV transmission line Culley to Knottsville (BREC/LGEE). Projects 1006 and 1007 are mutually exclusive |  |  | 51900000 |  |  | Formerly Culley to Knottsville | Vectren - F Fredrick |  | 2005-07-28 | [5 empty] | Y |  |  | Share
1257 | 2006-06-29 |  | E-IOK | Vectren (SIGE) | New transmission line Gibson (Cinergy) to AB Brown to Reid (BREC) | New transmission line Gibson (Cinergy) to AB Brown to Reid (BREC) | IN | KY |  | Increase Vectren transfer capability. Contingency Performance. |  | Budgeted |  | High |  |  |  |  | 73075000 |  |  | Dependent on mutliple TO approval, right-of-way, and regulatory approval. | Vectren - F Fredrick |  | 2006-06-29 | [5 empty] | Y
1258 | 2006-06-29 |  | E-IOK | Vectren (SIGE) | Pigeon Creek 138/69 kV Substation | Pigeon Creek 138/69 kV Substation | IN |  |  | Load growth. |  | Budgeted |  | Low |  |  |  |  | 3400000 |  |  |  | Vectren - F Fredrick |  | 2006-06-29 | [5 empty] | Y
1259 | 2006-06-29 |  | E-IOK | Vectren (SIGE) | New transmission line Dubois to Newtonville | New transmission line Dubois to Newtonville | IN |  |  | Load growth. Contingency performance. |  | Approved |  | Med |  |  |  |  | 14400000 |  |  |  | Vectren - F Fredrick |  | 2006-06-29 | [5 empty] | Y
1205 | 2006-02-10 | 2006-01 | E-MIO | WPSC | Cheboygan II Breaker Station | Add a 69KV breaker in the line from Tower to Pelston | MI |  |  | Increase Reliability to Cheboygan Substation |  | Budgeted | Obtained | [11 empty] | 2006-02-10 | [5 empty] | Y
1206 | 2006-02-10 | 2006-02 | E-MIO | WPSC | Bass Lake - Lake County Line Rebuild | Line Rebuild to 795ACSR for future 138KV operation | MI |  |  | The Bass Lake to Lake County Transmission Station was projected to be loaded at 106% of rating in summer 05. |  | Budgeted | Obtained |  |  |  |  | 05-2006_BL-LC_795ACSR_Rebuild.idv | [6 empty] | 2006-02-10 | [5 empty] | Y
1207 | 2006-02-10 | 2006-03 | E-MIO | WPSC | Hersey - Osceola Line Re-rate | Rerate line to 75C | MI |  |  | The Hersey to Osceola line was projected to be loaded to 102% in summer 05. |  | Budgeted | Obtained |  |  |  |  | 04-2006_HY-OC_LineRerate.idv | [6 empty] | 2006-02-10 | [5 empty] | Y
1208 | 2006-02-10 | 2006-04 | E-MIO | WPSC | Oden 12MVAR Capacitor Bank | Add 12MVAR Capacitor Bank at Oden Substation | MI |  |  | For the loss of the Oden transformer, the voltage levels are below the criteria for N-1 contingencies in the area. The 12MVAR capacitor bank will be used for voltage support. |  | Budgeted | Obtained |  |  |  |  | 03-2006_Oden_12MVAR_Capbank.idv | [6 empty] | 2006-02-10 | [5 empty] | Y
1209 | 2006-02-10 | 2007-01 | E-MIO | WPSC | Hersey 69KV Ring Bus | Convert 6 breaker bus at Hersey to Ring Bus | MI |  |  | The exising Hersey breaker station is a very old design and vulnerable to outages. The design is a single bus arrangement which needs to be upgraded to increase reliability |  | Budgeted | Pending | [11 empty] | 2006-02-10 | [5 empty] | Y
1210 | 2006-02-10 | 2007-02 | E-MIO | WPSC | Lewiston II Breaker Station | Add a 69KV breaker in the line from Atlanta to Gaylord | MI |  |  | Increase Reliability to Lewiston Substation |  | Budgeted | Pending | [11 empty] | 2006-02-10 | [5 empty] | Y
1211 | 2006-02-10 | 2007-03 | E-MIO | WPSC | Grand Traverse - Grawn Line Rebuild | Line Rebuild to 795ACSR for future 138KV operation | MI |  |  | The Grand Traverse to Grawn line was projected to be overloaded to 101% for the summer of 05. |  | Budgeted | Pending |  |  |  |  | 06-2007_GV-GN_795ACSR_Rebuild.idv | [6 empty] | 2006-02-10 | [5 empty] | Y
1212 | 2006-02-10 | 2007-04 | E-MIO | WPSC | Alpine - Gaylord Line Re-rate | Rerate line to 75C | MI |  |  | The Alpine to Gaylord line is projected to be overloaded to 103% for the summer of 2005. |  | Budgeted | Pending |  |  |  |  | 08-2007_GY-AN_LineRerate.idv | [6 empty] | 2006-02-10 | [5 empty] | Y
1213 | 2006-02-10 | 2007-05 | E-MIO | WPSC | Vestaburg Capacitor Bank | Add 6MVAR Capacitor Bank at Vestaburg Substation | MI |  |  | Voltage problems were found in the Vestaburg area in the long range plan. |  | Budgeted | Pending |  |  |  |  | 07-2007_VB_6MVAR_Capbank.idv | [6 empty] | 2006-02-10 | [5 empty] | Y
1214 | 2006-02-10 | 2008-01 | E-MIO | WPSC | Garfield - Grawn Line Rebuild | Line Rebuild to 795ACSR for future 138KV operation | MI |  |  | The Garfield to Grawn is projected to be overloaded during the loss of either Grand Traverse #1 or #2 feeds or Transformers for summer 05. |  | Budgeted | Pending |  |  |  |  | 09-2008_GF-GN_795ACSR_Rebuild.idv | [6 empty] | 2006-02-10 | [5 empty] | Y
1215 | 2006-02-10 | 2008-02 | E-MIO | WPSC | Advance - Wilson Line Re-rate | Rerate line to 75C | MI |  |  | The 69KV transmission line from Advance to Wilson was projected to be overloaded in 2005 for the loss of the Oden transformer. |  | Budgeted | Pending |  |  |  |  | 10-2008_AD-WS_LineRerate.idv | [6 empty] | 2006-02-10 | [5 empty] | Y
1216 | 2006-02-10 | 2008-03 | E-MIO | WPSC | Garfield - Hall Street Line Re-rate | Rerate line to 75C | MI |  |  | The line was overloaded due to the loss of either Transformer at Grand Traverse for summer 05 |  | Budgeted | Pending |  |  |  |  | 11-2008_GF-HL_LineRerate.idv | [6 empty] | 2006-02-10 | [5 empty] | Y
1217 | 2006-02-10 | 2008-04 | E-MIO | WPSC | Grawn 69KV Ring Bus | Convert 4 breaker bus at Grawn to Ring Bus | MI |  |  | The exising Atlanta breaker station is a very old design and vulnerable to outages. The design is a single bus arrangement which needs to be upgraded to increase reliability. |  | Budgeted | Pending | [11 empty] | 2006-02-10 | [5 empty] | Y
1218 | 2006-02-10 | 2009-01 | E-MIO | WPSC | Atlanta 69KV Ring Bus | Convert 4 breaker bus at Atlanta to Ring Bus | MI |  |  | The exising Grawn breaker station is a very old design and vulnerable to outages. The design is a single bus arrangement which needs to be upgraded to increase reliability. |  | Budgeted | Pending | [11 empty] | 2006-02-10 | [5 empty] | Y
1219 | 2006-02-10 | 2009-02 | E-MIO | WPSC | Lake County - Star Lake Line Rebuild | Line Rebuild to 795ACSR for future 138KV operation | MI |  |  | The Lake County to Star Lake line was projected to be overloaded in summer 05. |  | Budgeted | Pending |  |  |  |  | 12-2009_LC-SL_795ACSR_Rebuild.idv | [6 empty] | 2006-02-10 | [5 empty] | Y
1220 | 2006-02-10 | 2009-03 | E-MIO | WPSC | Copemish - Bass Lake Line Rerate | Rerate line to 75C | MI |  |  | The Copemish to Bass Lake line was projected to be overloaded in summer 05. |  | Budgeted | Pending |  |  |  |  | 13-2009_CH-BL_LineRerate.idv | [6 empty] | 2006-02-10 | [5 empty] | Y
1221 | 2006-02-10 | 2010-01 | E-MIO | WPSC | Redwood - New Era Line Rebuild | Line Rebuild to 795ACSR for future 138KV operation | MI |  |  | The Redwood to New Era Line is expected to be overloaded in the summer of 2010. |  | Budgeted | Pending |  |  |  |  | 14-2010_RW-NE_795ACSR_Rebuild.idv | [6 empty] | 2006-02-10 | [5 empty] | Y
1222 | 2006-02-10 | 2010-02 | E-MIO | WPSC | Lake County - Star Lake Line Rebuild | Convert 4 breaker bus at Lake County to Ring Bus | MI |  |  | The exising Lake County breaker station is a very old design and vulnerable to outages. The design is a single bus arrangement which needs to be upgraded to increase reliability. |  | Budgeted | Pending | [11 empty] | 2006-02-10 | [5 empty] | Y
1226 | 2006-03-15 | 2007-06 | East | WPSC | Kalkaska Gen - Westwood Line Rebuild | Kalkaska Gen - Kalkaska JCT - Westwood Line Rebuild. Summer Rating 102.4 MVA | MI |  |  | The proposed project is needed to address the impending and potential overloads expected in 2006 shoulder peak time periods. Kalksaska Gen to Kalkaska Jct is loaded to 115.6% and Kalkaska Jct to Westwood is loaded to 105.4%. |  | Pending | Not Required. | low | 0% | n/a | North One-line.dwg | KM-WW_Rebuild |  |  |  | Redwood 138/69 transformer #2 is not in Facility table |  | ANR El Paso SIS 013106.pdf | 2006-02-07 |  | Y | 2006-03-07 |  |  | Y | 2006-06-15
1227 | 2006-03-15 | 2007-08 | East | WPSC | Gaylord Gen - Bagley Junction | Gaylord Gen - Bagley Junction Rebuild. Summer Rating 102.4 MVA | MI |  |  | The proposed project is needed to address the impending and potential overloads expected in 2006 shoulder peak time periods. Gaylord Gen to Bagley Jct is loaded to 103.6% under the Atlanta 138 to Gaylord 138 line outage contingency. |  | Pending | Not Required. | low | 0% | n/a | North One-line.dwg | GY-BYX_Rebuild | [5 empty] | ANR El Paso SIS 013106.pdf | 2006-02-07 |  | Y | 2006-03-07 |  |  | Y | 2008-02-01
1228 | 2006-03-16 | 2008-05 | East | WPSC | ANR Elpaso New Load | Add 14MW load off of Wolverine's Westwood Junction | MI |  |  | A natural gas compressor station is installing electric motors to replace their existing gas motors to drive their compressors. |  | Pending | Not Required. |  |  |  |  | 2008-ANR Load.idv |  |  |  | Approval letter dated 4/3/06. |  |  | 2006-02-07 |  | Y | 2006-03-07 |  |  | Y
1229 | 2006-03-16 | 2006-05 | East | WPSC | Plains Junction Breaker Station | Replace Relaying and Breakers at Plains Junction Substation | MI |  |  | Plains Junction substation is a very old design with old oil breakers and relaying. An upgrade is necessary to improve reliability |  | Approved | Not Required. | [17 empty] | Y
1230 | 2006-03-16 | 2006-06 | East | WPSC | White Cloud Breaker Station | Replace Relaying and Breakers at White Cloud Substation | MI |  |  | White Cloud substation is a very old design with old oil breakers and relaying. An upgrade is necessary to improve reliability |  | Approved | Not Required. | [17 empty] | Y
1231 | 2006-03-16 | 2006-07 | East | WPSC | Superior Corn Substation | Add new load point neer Wolverine's Odessa Substation | MI |  |  | New Customer |  | Approved | Not Required. |  |  |  |  | 02-2006_Superior_Substation_Addition.idv | [12 empty] | Y
1272 | 2006-07-13 | 2010-03 | East | WPSC | Redwood 75MVA Transformer | Add 75MVA Transformer at Redwood Substation a separate line from Redwood Junction will be ran to energize the transformer. | MI |  |  | The existing 138/69KV transformer at Redwood becomes overlaoded for the loss of the Redwood or Lake County transformer. |  | Pending | Not Required |  |  |  |  | 01-Redwood Transformer.idv | [6 empty] | 2006-07-13 | [5 empty] | Y
1273 | 2006-07-27 | 2007-09 | East | WPSC | Alpine to Elmira Line Re-rate | Rerate the line from Alpine Sub to Elmira Sub for an operating temperature of 75C | MI |  |  | Line becomes overloaded under contingency in 2006 |  | Pending | Not Required |  |  |  |  | 2007 AN-EL rerate.idv | [12 empty] | Y
1274 | 2006-07-27 | 2007-10 | East | WPSC | Allendale to Blendon Line Re-rate | Rerate the line from Allendale Sub to Blendon Sub for an operating temperature of 75C | MI |  |  | Line becomes overloaded under contingency in 2006 |  | Pending | Not Required |  |  |  |  | 2007 AL-BQ rerate.idv | [12 empty] | Y
1275 | 2006-07-27 | 2007-11 | East | WPSC | Boyne City to Wilson Line Re-Rate | Rerate the line from Boyne City Sub to Wilson Sub for an operating temperature of 75C | MI |  |  | Line becomes overloaded under contingency in 2006 |  | Pending | Not Required |  |  |  |  | 2007 BC-WS rerate.idv | [12 empty] | Y
1276 | 2006-07-27 | 2010-04 | East | WPSC | Burnips to Goodwin Line Re-Rate | Rerate the line from Burnips Sub to Goodwin Sub for an operating temperature of 75C | MI |  |  | Line becomes overloaded under contingency in 2010 |  | Pending | Not Required |  |  |  |  | 2010 BP-GW rerate.idv | [12 empty] | Y
1277 | 2006-07-27 | 2011-01 | East | WPSC | Wayland to Goodwin Line Re-Rate | Rerate the line from Wayland Sub to Goodwin Sub for an operating temperature of 75C | MI |  |  | Line becomes overloaded under contingency in 2011 |  | Pending | Not Required |  |  |  |  | 2011 WD-GW rerate.idv | [12 empty] | Y
56 | 2006-03-27 | 41 | N-NM | XEL | Chisago - Apple River | Chisago - Lindstrom - Shafer- Lawrence Creek 69 kV rebuild to 115 kV, Lawrence Creek - St Croix Falls - Apple River 69 kV rebuild to 161 kV. New Lawrence Creek 161/115/69 kV substation | MN |  |  | 1. East-central Minnesota load serving: The Arden Hills-St Croix Falls-Apple River 69 kV line cannot serve load for outage of either end. Severe line overloads (189%) and low voltages (0.7 pu) occur, if all load on the line is attempted to be served from a single source (2002 summer peak loads). 2. Northwestern Wisconsin load serving: Same 69 kV load serving issue as East-central MN (2002 summer peak loads). Also has low Apple River 161 kV voltage (0.89 pu) for load serving issue as East-central MN. Also has low Apple River 161 kV voltage (0.89 pu) for outage outage of Apple River-Pine Lake-Crystal Cave 161 kV line. 3. Northern Wisconsin load serving (2002 summer peak loads): Outage of Stinson 115 kV bus may cause voltage collapse in Northern Wisconsin depending on Bay Front generation level in the Winter. With no Bay Front or Flambeau Jet generation, the Northern region is at risk 145 hours in 2002. Bay Front generation at 26 MW reduces risk to 9 hours in 2002. Cornell-Holcombe 115 kV may overload (141%) for outage of Stone Lake-Washco 161 kV line. | XEL Chisago-Apple River.doc | Approved | Required | High | 0 | 1. Chisago-Apple River 69 kV line rebuild 2. Reconfigure 69 kV system and add reactive support 3. Distributed generation which was cost prohibitive | [5 empty] | In service date changed to allow further study and refinement of the scope of work. | XEL - Jason Standing |  |  |  |  | 2003-06-25 |  |  | Y |  |  | Excluded
265 | 2006-07-12 | 260 | N-NM | XEL | Glencoe - McLeod 115 | Glencoe - McLeod 115 ckt 1, Sum rate 310 | MN |  |  | Loss of Carver County transformer may result in voltages below 90 % beginning in 2001 for Waconia transmission sub-system. |  | Approved | Not Required | [8 empty] | Energization expected in July 2006 | XEL - Walt Grivna |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
267 | 2006-07-12 | 262 | N-NM | XEL | Lawrence - Minnehaha 115 | Lawrence - Minnehaha 115 ckt 1, Sum rate 310 | SD |  |  | Outage of the Split Rock-W Sioux/Split Rock-Cherry Creek double-circuit 115 kV line leaves most of the Sioux Falls area load served through the Lawrence-Lincoln Co 115 kV line. Lawrence-Minnehaha 115 kV may overload to 115% of it's continous of 240 MVA at projected 2003 summer peak loads. The line work has been completed and now has a rating of 310 MVA (summer continous rating). Equipment at Minnehaha substation still needs to be upgraded. |  | Approved | Not Required | [8 empty] | This project is expected to be in service in May 1st 2007 | XEL - Walt Grivna |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
268 | 2006-07-12 | 263 | N-NM | XEL | Minnehaha - Lincoln County 115 | Minnehaha - Lincoln County 115 ckt 1, Sum rate 310 | SD |  |  | Outage of the Split Rock-W Sioux/Split Rock-Cherry Creek double-circuit 115 kV line leaves most of the Sioux Falls area load served through the Lawrence-Lincoln Co 115 kV line. Minnehaha -Lincoln County 115% may overload to 101% of it's sag limit. Equipment at Minnehaha substation needs to be upgraded as well. |  | Approved | Not Required | [8 empty] | This project is expected to be in service in May 1st 2007 | XEL - Walt Grivna |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
269 | 2006-07-12 | 264 | N-NM | XEL | Prairie Island - Red Rock 345 | Prairie Island - Red Rock 345 ckt 2, Sum rate 1198 | MN |  |  | Prairie Island - Red Rock #2 345 kV line may overload load (119% of it’s continous rating 598 MVA at 2004 summer peak loads for a double circuit contingency of the Prairie Island - Blue Lake 345 kV line and the Prairie Island - Red Rock #1 345 kV line |  | Approved | Not Required | [8 empty] | Capacity raised to 691 sufficient for meeting 2006 requirements remainder of upgrade to be in service 6-1-07 | XEL - Walt Grivna |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
270 | 2006-07-12 | 265 | N-NM | XEL | Champlin - Champlin Tap 115 | Champlin - Champlin Tap 115 ckt 1, Sum rate 310 | MN |  |  | Loss of Elm Creek to Parkers Lake 345 kV, Sherco - Coon Creek 345 kV #1 and Coon Creek 345/115 kV trx #9 overloads Champlin - Champlin Tap 115 kV to 125% of it's emergency rating of 254 MVA at forecasted 2004 summer peak loads |  | Approved | Not Required | [8 empty] | Expected to be in service in June 2007 | XEL - Walt Grivna | [7 empty] | Y |  |  | Excluded
271 | 2006-07-12 | 266 | N-NM | XEL | Hungry Hollow - Ballard Corner 115 | Hungry Hollow - Ballard Corner 115 ckt 1, Sum rate | MN |  |  | The existing Wilmarth-Madelia (Rapidan) 69 kV line consists of 80 miles of line exposure, with 11 substations affected by each tripout. It is consistently among the worst-performing lines in the NSP system, due to length and condition; some of the line dates from 1931. This re-configuration also prevents low voltage conditions (<.90 pu) following loss of the Wilmarth-Hungry Hollow 69 kV segment. |  | Approved | Not Required | [8 empty] | This project will be done in 2008 along with GRE's Hungry Hollow switching station. | XEL - Walt Grivna | [7 empty] | Y |  |  | Not Shared
272 | 2006-03-27 | 267 | N-NM | XEL | Air Lake - Vermillion River 115 | Air Lake - Vermillion River 115 ckt 1, Sum rate 200 | MN |  |  | At 2006 summer peak projected loads, Loss of Burnville to Riverwood 115 kV may result in overloads of the following facilities: 1. Williams Pipeline to Fischer 115 kV may load to 114% of it's continous rating of 191 MVA 2. Williams Pipeline to Apple Valley West 115 kV may load to 116% of it's continous rating of 191 MVA 3. Johnny Cake - Apple Valley W 115kV may load to 116 % of it's continous rating of 191 MVA. Loss of Black Dog to Riverwood 115 kV may load Koch - Apple Valley E 115kV to 114 % of it's continous rating of 315 MVA. Loss of Koch - Apple Valley E 115kV may overload Riverwood - Black Dog 115kV to 124% of it's continous rating of 310 MVA and Riverwood - Burnsville 115kV to 113% of it' continous rating of 310 MVA |  | Approved | Obtained | High | [7 empty] | Working with the City of Farmington. | XEL - Jason Standing |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Service
366 | 2006-03-27 | St Cloud | N-NM | XEL | Sherburne Co Area 115 kV project | Upgrade Sherco - Monticello 115 and Sherco - St Cloud 115 kV lines, new Sherco 345/115 transformer | MN |  |  | At 2004 projected summer peak projected loads, Loss of the 115 kV double circuit from Benton County to Granite City may overload Monticello to Salida to 130% of it's emergency rating of 154 MVA. Salida to St. Cloud 115 kV may overload to 127 % of it's emergency rating of 154 MVA. At 2009 projected summer peak loads, Monticello 345/230 kV transformer may overload to 110% of it's emergency rating of 436 MVA. | MTEP05 report, Sherco generation increase outlet study | Approved | Not Required | High | 0% | Change existing 345/230kV 336 MVA transformer at Monticello to 2 x 448 MVA units. Rebuild Monticello to Salida Crossing to 194 industrial Park to St Cloud 115kV line to 795 kcm ACSS Monticello change out wavetrap, CT and disconnect to raise rating of 230KV line from Monticello - Benton from 400 to 472 MVA. | [5 empty] | budget deferrals caused by numerous generation interconnection obligations | XEL - Jason Standing |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
377 | 2006-07-12 | Wind 425 | N-NM | XEL | Xcel Energy Wind 425 MW project | Buffalo Ridge (SW MN) 425 MW of Generation Outlet: Lakefield to Fox Lake new 161 kV, Spring 06 Bird Island to Franklin rebuild 69 kV, Complete Chanarambie - Lake Yankton - Lyon Co. new 115 kV, Complete Lyon substation, Complete Lyon County 115 kV 2X30 Mvar capacitors, Complete Wilmarth to Martin Co. 345 kV upgrade, Complete Paynesville to Wakefield 115 kV rebuild, Complete Willmar to Kerkhoven 115 kV rebuild, Complete Summit to Dome to Loon Tap 115 kV rebuild, Complete Grant Co. to Brandon 115 kV rebuild, Complete Alexandria to Douglas Co. 115 kV rebuild, Dec 05 Willmar Transformer, Dec 05 Minn Valley Transformers, Dec 05 Black Dog Transformer, Complete Paynesville Transformer, Complete Lake Yankton substation and SVC, Complete Lake Yankton 115 kV 4X20 Mvar capacitors, Complete Brandon to Alexandria 115 kV rebuild, Complete Loon Tap to West Faribault 115 kV rebuild , Complete Troy substation 69 kV new, Complete Lyon County to Marshall 115 kV upgarde, Complete Fox Lake substation upgrade, Spring 2006 West Faribault substation upgrade, Dec 05 Bird Island substation upgrade, Complete Franklin substation upgrade, Complete Douglas substation upgrade , March 05 | MN |  |  | Transmission to create outlet for SW Minnesota wind generation | XEL Wind 425 MW project.doc | Approved | Obtained | Low | 70% | [6 empty] | The Lakefield - Fox lake 2nd Circuit will be completed by Nov 2006. This project is under construction. The Minn Valley- Redwood Falls 115 kV upgrade will be completed by 12-1-06. | XEL - Walt Grivna |  |  |  |  | 2003-06-25 |  |  | Y |  |  | Service
417 | 2006-07-12 | 309 | N-NM | XEL | Westgate 115, 80 MVAR Capacitor | Westgate 115, 80 MVAR Capacitor | MN |  |  | Loss of the double circuit from Westgate-Eden Prairie 115kV may cause voltages to fall below 92% at Westgate 115kV, Deephaven 69kV, and Excelsior for 2008 forecast summer peak loads |  | Approved | Not Required | [8 empty] | Under Construction. This project is expected to be completed by mid 2007 | XEL - Walt Grivna |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
609 | 2006-07-12 |  | N-NM | XEL | Long Lake - Oakdale 115 kV line | Long Lake - Oakdale 115 kV line | MN |  |  | For 2004 projected summer peak loads, post-contingent loading (outage of Red Rock - Woodbury 115 kV) is about 107% of it's emergency rating of 239 MVA (equipment at Long Lake limits rating of line to 239 MVA) |  | Approved | Not Required | [8 empty] | This project is expected to be completed by mid 2007 | XEL - Walt Grivna | [7 empty] | Y |  |  | Excluded
671 | 2006-07-12 |  | N-NM | XEL | Oakdale - Tanners Lake 115 | Oakdale - Tanners Lake 115 ckt # 1 | MN |  |  | For projected 2004 summer peak loads, post-contingent loading (outage of Red Rock - Woodbury 115 kV) is about 100% of its emergency rating of154 MVA |  | Approved | Not Required | [8 empty] | This project is expected to be complete in mid 2007. Load has not developed. | XEL - Walt Grivna |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Excluded
673 | 2006-07-12 |  | N-NM | XEL | Champlin Tap - Crooked Lake 115 | Champlin Tap - Crooked Lake 115 ckt # 1 | MN |  |  | For projected 2009 peak loads, Loss of Coon Creek – Parkwood 115 kV overloads Champlin Tap-Crooked Lake 115 kV to 100% of it's emergency rating of 207 MVA |  | Approved | Not Required | [8 empty] | This project is expected to be complete in mid 2008. Load has not developed. | XEL - Walt Grivna | [7 empty] | Y |  |  | Not Shared
674 | 2006-07-12 |  | N-NM | XEL | High Bridge - Rogers Lake 115 | High Bridge - Rogers Lake 115 ckt # 1 | MN |  |  | To provide outlet for 2009 High Bridge increased generation outlet under certain operating conditions |  | Approved | Not Required | [8 empty] | Under construction. This project is expected to be completed by mid 2008. | XEL - Walt Grivna | [7 empty] | Y |  |  | Service
675 | 2006-07-12 |  | N-NM | XEL | Rebuild Westgate to Scott County 69 kV to 115 kV | Upgrade 20.1 miles Westgate-Deephaven-Excelsior-Scott County 69kV to 115 kV using 795 ACSS conductor, Upgrade 2 miles Westgate-Eden Prairie 115kV #1 and #2 to 400MVA (PrjID 606), Substation work at Deephaven, Excelsior and Scott County. | MN |  |  | Loss of Scott County source may overload Westgate to Deephaven 69 kV to 100% of it's planned rating of 84 MVA (continous and emergency rating) at 2011 projected summer peak loads. For this outage, the loads would be served radially from Westgate | P675 XEL Westgate to Scott Co | Not Budgeted | Required | Low | 0% | 115 kV Westgate to Glen Lake to Gleason Lake | [5 empty] | Project can not be physically constructed as planned. Plans under re evaluation. New Generation added in area has mitigated the need for this project. | XEL - Walt Grivna | XEL 2003 Glen Lake area transmission study | [6 empty] | Y |  |  | Share
751 | 2005-07-19 |  | N-NM | XEL | Nobles Co 34.5 kV -50 MVAR Reactor #1 | Nobles Co 34.5 kV -50 MVAR Reactor #1 | MN |  |  | Transmission to create outlet for SW Minnesota wind generation | [20 empty] | Y
752 | 2005-07-19 |  | N-NM | XEL | Edgewater 69 kV 5.4 MVAR Capacitor | Edgewater 69 kV 5.4 MVAR Capacitor | WI |  |  | For projected 2007 summer peak loads, the capacitor is needed to alleviate low voltage in the vicinity of the Edgewater substation in Northwest Wisconsin during outage of the primary transmission source to this 69 kv system | [20 empty] | Y
778 | 2006-07-12 |  | N-NM | XEL | Nobles Co 34.5 kV 50 Mvar Reactor #2 | Nobles Co 34.5 kV 50 Mvar Reactor #2 | MN |  |  | Transmission to create outlet for SW Minnesota wind generation |  | Approved | Not Required | [8 empty] | Under construction. This project is expected to be completed by the end of 2007. Nobles Co substation will be built as part of the 825MW wind development and its expected to be inservice by end of 2007 | XEL - Walt Grivna |  |  |  |  | 2005-06-16 |  |  | Y
780 | 2006-07-12 |  | N-NM | XEL | Lakefield Gen - Wilmarth Series Compensation | Fieldon Township 345 kV Series Capacitor 20 ohms | MN |  |  | Transmission to create outlet for SW Minnesota wind generation | See Transmission outlet analysis for SW Minnesota (Buffalo Ridge Area) generation addition volume 1 and volume 2 | Approved | Obtained | High | 0% | See Transmission outlet analysis for SW Minnesota (Buffalo Ridge Area) generation addition volume 1 and volume 2 | [5 empty] | This project is expected to be completed by the end of 2007. | XEL - Walt Grivna |  |  |  |  | 2005-06-16 |  |  | Y |  |  | Service
1031 | 2004-12-23 |  | N-NM | XEL | Garwind McNeilus generator TSR upgrades | TSR conditional upgrades for delivery of G171, G239, G242 | MN |  |  | Required for TSR | [20 empty] | Y
1034 | 2005-09-01 |  | N-NM | XEL | Loon Lake 115/69 kV transformer upgrade | Replace Loon Lake 115/69 kV transformer with 112 MVA | MN | [23 empty] | Y
1024 | 2005-10-12 | SE MN - SW WI | N-NM | XEL/DPC/RPU | Southeast MN - Southwest WI upgrades | Construct Prairie Island-Rochester-North LaCrosse 345 kV line, Alma-LaCross tap-Genoa 161 rebuild, Adams-Harmony 161 rebuild, North Rochester 354/161 transformer, North LaCrosse 345/161 transformer | MN | WI |  | Rochester and LaCrosse load serving | [20 empty] | Y |  |  | Share
1203 | 2006-01-25 | SW MN - TC EHV | N-NM | XEL/GRE | Southwest Minnesota -Twin Cities EHV Development | Brookings County -Lyon County-Franklin (Double Crt) -Helena-Lk Marion-Hampton Corner 9 (Single Crt) 345 kV | MN |  |  | Load Serving | [14 empty] | 2006-01-25 | [5 empty] | Y |  |  | Share
Includes generator interconnection projects
Includes sub-transmission projects

## q_Facility_Planned_Proposed
Facil ID | Record Date | Facility Type | Region | Reporting Source | PrjID | Prj Rec Date | Owner PrjID | Expected ISD | From Sub or Location | To Sub or Device Description | Ckt | Voltage | Volt Low | Sum Rate | Upgrade Desc | Map Grid | State | Miles Upg | Miles New | Need Load | Need Gen Int | Need TSR | Need Other | Plan Status | Estimated Cost | Est Type | Cancellation Reason | FTR Usage | Comments | Submit Date | Submit Study | Last Change | TO, Gen Int or TSR Study | MISO AppA | MAPP Form | Public Flag | Idev File | Upgrade Type | TSR Cond Upg
1791 | 2005-11-18 | GEN | West | ALTW | 1141 | 2005-11-18 |  | 2003-05-01 | MRES | generator | 1 |  |  | 2 | new generator |  | MN |  |  |  | 100 |  |  | Under Construction |  |  |  |  | 34216 |  |  |  | G270 | Y | N | Y |  | Generator
1239 | 2005-09-08 | BR | N-NM | ALTW | 1032 | 2005-09-08 |  | 2005-12-30 | Magnolia 161-69 kV | transformer | 1 | 161 | 69 | 56 |  | G7 | MN |  |  | 100 |  |  |  | Planned | 150000 | [8 empty] | Y | Y | Y
2104 | 2006-01-31 | BR | N-NM | ALTW | 1204 | 2006-01-31 |  | 2006-10-01 | Adams | Rochester | 1 | 161 |  | 201/221 MVA | replace termination jumpers at Adams | I7 | MN |  |  |  |  | 100 |  | Planned | 5000 | Planning MISO |  |  | 221 emergency rating. submitted by DPC | 2006-01-31 |  |  |  | Y | Y | Y |  |  | Y
1797 | 2005-11-18 | GEN | West | ALTW | 1147 | 2005-11-18 |  | 2006-12-31 | Zilkha (Triboji) | generator |  |  |  | 100 | new generator |  | IA |  |  |  | 100 |  |  | Planned |  |  |  |  | 34137 |  |  |  | G298 | Y | N | Y |  | Generator
189 | 2005-11-28 | BR | N-ITWG | ALTW | 90 | 2005-07-11 | 69 | 2007-06-01 | Emery | Lime Creek | 2 | 161 |  | 326 | New Facility | H7 | IA |  | 26 | 100 |  |  |  | Planned | 8000000 |  |  |  | Contractual and logistic issues causing delay |  |  |  | A102 | Y | Y | Y |  |  | Y
665 | 2005-07-11 | BR | N-ITWG | ALTW | 589 | 2006-03-10 |  | 2007-06-01 | Timber Creek | Highland Acres | 1 | 161 |  | 291 | New Facility |  | IA | 3 |  | 100 |  |  |  | Proposed | 650000 | [8 empty] | Y | Y | Y
1415 | 2005-01-18 | BR | N-ITWG | ALTW | 1035 | 2005-01-18 |  | 2007-06-01 | Wyoming 161/69 | transformer | 1 | 161 | 69 | 83 |  |  | IA | [6 empty] | Proposed | 1757000 | Planning MISO | 10407000 |  |  | 2005-01-18 |  |  |  | Y | N | Y
3000 | 2006-06-23 | DV | N-ITWG | ALTW | 746 | 2005-07-11 |  | 2009-12-31 | Huxley Industrial | Capacitor |  | 69 |  | 9.6 Mvar | New Facility | H8 | IA |  |  | 100 |  |  |  | Planned | 438000 | Planning MISO |  |  | Determined it was not needed in 2006 as earlier planned |  |  |  |  | Y | Y | Y
1856 | 2005-12-05 | BR | West | ALTW |  |  |  |  | Mason City Armor | Emery North |  | 69 |  |  | Rebuild existing line |  | IA |  |  |  |  | 100 |  | Planned |  |  |  |  | Submitted by MISO |  |  |  | A031, A207 | Y | N | Y |  |  | Y
1398 | 2006-07-05 | BR | C-CSILL | Ameren | 707 | 2006-03-17 |  | 2006-11-01 | Adair (Install Breaker for Thomas Hill Line) | Install 161 kV Breaker at Adair |  | 161 |  | 281 | new 161 kV breaker | I9 | MO |  |  | 100 |  |  |  | Under Construction | 335900 | Eng | [5 empty] | Ameren - J Sullivan |  | Y | N | Y
46 | 2006-03-17 | BR | C-CSILL | Ameren | 77 | 2005-07-11 | 54 | 2006-12-01 | Callaway | Franks | 1 | 345 |  | 1606 | new 345 kV line | I10 | MO |  | 54 | 100 |  |  |  | Under Construction | 29966200 | Eng | [5 empty] | Ameren - C Stepanek |  | Y | N | Y
831 | 2006-07-05 | BR | C-CSILL | Ameren | 856 | 2005-07-11 |  | 2006-12-01 | Osage 138 kV Substation | Eldon | 1 | 138 |  | 200 | Replace bus conductor at Osage Substation | I11 | MO |  |  | 100 |  |  |  | Planned | 65000 | Eng | 30367100 |  |  |  |  | Ameren - J Sullivan |  | Y | N | Y
1942 | 2006-03-17 | BR | C-CSILL | Ameren | 1240 | 2006-03-17 |  | 2007-03-01 | Mattoon, West | Install 138 kV Breaker at Mattoon, West | 1 | 138 |  |  | Install 138 kV Breaker to connect Wind Farm | K10 | IL |  |  |  | 100 |  |  | Planned | 555400 | Eng |  |  |  | 2006-03-17 | MTEP06 P2 | Curt Stepanek |  | Y | N | Y
56 | 2006-03-17 | BR | C-CSILL | Ameren | 143 | 2006-03-17 |  | 2007-06-01 | Cahokia | N. Coulterville | 1 | 230 |  | 400 | increase ground clearance | J11 | IL | 45 |  | 100 |  |  |  | Planned | 476700 | Eng | [5 empty] | Curt Stepanek |  | Y | N | Y
397 | 2006-03-17 | BR | C-CSILL | Ameren | 149 | 2006-03-17 |  | 2007-06-01 | Mason | Sioux | 1 | 345 |  |  | breaker addition at Mason | J11 | MO |  |  | 100 |  |  |  | Planned | 605900 | Eng | [5 empty] | Curt Stepanek |  | Y | N | Y
1399 | 2006-03-17 | BR | C-CSILL | Ameren | 708 | 2006-03-17 |  | 2007-06-01 | Casey | Breed | 1 | 345 |  | 1332 | reconductor river crossing | L10 | IL | 0.23 |  |  |  |  | 100 | Planned | 303900 | Eng |  |  | Coordinate construction activities and relay changes with AEP |  |  | Ameren - C Stepanek |  | Y | N | Y
1401 | 2006-03-17 | BR | C-CSILL | Ameren | 710 | 2005-07-11 |  | 2007-06-01 | Kinmundy | Salem | 1 | 138 |  | 240 | increase ground clearance | K10 | IL | 10.3 |  | 100 |  |  |  | Proposed | 661200 | Eng |  |  | Project need and timing under review |  |  | Ameren - C Stepanek |  | Y | N | Y
1402 | 2006-03-17 | BR | C-CSILL | Ameren | 711 | 2006-03-17 |  | 2007-06-01 | Wood River | Gillespie | 1 | 138 |  | 240 | reconductor | K10 | IL | 7.5 |  | 100 |  |  |  | Planned | 939500 | Eng | [5 empty] | Curt Stepanek |  | Y | N | Y
1403 | 2006-03-17 | BR | C-CSILL | Ameren | 712 | 2006-03-17 |  | 2007-06-01 | Mason | Labadie-Mason-3 Term. Equipment replacement | 1 | 345 |  |  | terminal equipment upgrade at Mason | J11 | MO |  |  | 100 |  |  |  | Planned | 184100 | Eng | [5 empty] | Curt Stepanek |  | Y | N | Y
3094 | 2006-03-17 | DV | C-CSILL | Ameren | 783 | 2005-07-11 |  | 2007-06-01 | Robinson-Marathon | Cap. - Increase 18 Mvar to 36 Mvar |  | 138 |  | 36 Mvar | increase size of existing 138 kV capacitor | L10 | IL |  |  | 100 |  |  |  | Proposed | 151900 | Eng |  |  | Project need and timing under review |  |  | Ameren - C Stepanek |  | Y | N | Y
832 | 2006-03-17 | BR | C-CSILL | Ameren | 857 | 2005-07-11 |  | 2007-06-01 | Rush Island | Joachim | 1 | 345 |  | 1200 | Replace terminal equipment at Rush Island | J11 | MO |  |  | 100 |  |  |  | Planned | 283200 | Eng | [5 empty] | Curt Stepanek |  | Y | N | Y
833 | 2006-03-17 | BR | C-CSILL | Ameren | 858 | 2005-07-11 |  | 2007-06-01 | Sioux | Huster | 1 | 138 |  | 214 | Increase ground clearance | J10 | MO | 6 |  | 100 |  |  |  | Planned | 1024500 | Eng | 5186300 |  |  |  |  | Curt Stepanek |  | Y | N | Y
65 | 2006-03-17 | BR | C-CSILL | Ameren | 78 | 2006-03-17 | 55 | 2008-06-01 | Jefferson City 345/161 | transformer | 1 | 345 | 161 | 450 | new 345/161 kV transformer | I11 | MO |  |  | 100 |  |  |  | Planned | 6256900 | Eng |  |  | Delays in obtaining suitable line route |  |  | Ameren - C Stepanek |  | Y | N | Y
59 | 2006-03-17 | BR | C-CSILL | Ameren | 78 | 2006-03-17 | 55 | 2008-06-01 | Loose Creek | Jefferson City | 1 | 345 |  | 1606 | new 345 kV line | I11 | MO |  | 15 | 100 |  |  |  | Planned | 10210700 | Eng |  |  | Delays in obtaining suitable line route |  |  | Ameren - C Stepanek |  | Y | N | Y
392 | 2006-03-17 | BR | C-CSILL | Ameren | 144 | 2006-03-17 |  | 2008-06-01 | Crab Orchard | Marion South | 1 | 138 |  | 399 | reconductor | K11 | IL | 9.1 |  | 100 |  |  |  | Planned | 2712300 | Eng |  |  | Possible scope change in corrective action plan |  |  | Ameren - C Stepanek |  | Y | N | Y
398 | 2006-03-17 | BR | C-CSILL | Ameren | 150 | 2006-03-17 | PS gen | 2008-06-01 | Rush Island | Baldwin | 1 | 345 |  | 1793 | terminal at Rush Island & river crossing only | J11-K11 | IL |  | 2 |  | 100 |  |  | Planned | 1615100 |  |  |  | Project timing dependent on customer, permits, and right-of-way acquisition |  |  | Ameren - C Stepanek | IP04 | Y | N | Y |  | Net?
400 | 2006-03-17 | BR | C-CSILL | Ameren | 153 | 2006-03-17 |  | 2008-06-01 | CEE Tap | Watson | 1 | 138 |  | 370 | reconductor | J11 | MO | 0.8 |  | 100 |  |  |  | Planned | 311400 | Eng | [5 empty] | Ameren - C Stepanek |  | Y | N | Y
401 | 2006-03-17 | BR | C-CSILL | Ameren | 155 | 2006-03-17 |  | 2008-06-01 | Joachim 345/138 kV | transformer | 1 | 345 | 138 | 560 | new 345/138 kV transformer | J11 | MO |  |  | 100 |  |  |  | Planned | 12963300 | Eng |  |  | Delays in obtaining suitable substation site |  |  | Ameren - C Stepanek |  | Y | N | Y
1406 | 2006-03-17 | BR | C-CSILL | Ameren | 715 | 2005-07-11 |  | 2008-06-01 | Wildwood | Gray Summit | 1 | 138 |  | 415 | reconductor | J11 | MO | 0.14 |  | 100 |  |  |  | Proposed | 64250 | Eng |  |  | Project need and timing under review |  |  | Ameren - C Stepanek |  | Y | N | Y
1407 | 2006-03-17 | BR | C-CSILL | Ameren | 716 | 2005-07-11 |  | 2008-06-01 | Wildwood | Gray Summit | 2 | 138 |  | 415 | reconductor | J11 | MO | 0.14 |  | 100 |  |  |  | Proposed | 64250 | Eng |  |  | Project need and timing under review |  |  | Ameren - C Stepanek |  | Y | N | Y
1408 | 2006-03-17 | BR | C-CSILL | Ameren | 717 | 2005-07-11 |  | 2008-06-01 | Conway | Orchard Gardens | 1 | 138 |  | 240 | increase ground clearance | J11 | MO |  |  | 100 |  |  |  | Proposed | 100000 |  |  |  | Project need and timing under review |  |  | Ameren - C Stepanek, K Thammineni (cost) |  | Y | N | Y
1409 | 2006-03-17 | BR | C-CSILL | Ameren | 718 | 2005-07-11 |  | 2008-06-01 | Conway | Orchard Gardens | 2 | 138 |  | 240 | increase ground clearance | J11 | MO |  |  | 100 |  |  |  | Proposed | 100000 |  |  |  | Project need and timing under review |  |  | Ameren - C Stepanek, K Thammineni (cost) |  | Y | N | Y
1410 | 2006-03-17 | BR | C-CSILL | Ameren | 719 | 2006-03-17 |  | 2008-06-01 | Labadie Plant | Replace 2-345 kV Breakers |  | 345 |  |  | replace existing 345 kV breakers | J11 | MO |  |  | 100 |  |  |  | Planned | 1897100 | Eng | [5 empty] | Curt Stepanek | Gen | Y | N | Y |  | Int or Net?
834 | 2006-03-17 | BR | C-CSILL | Ameren | 859 | 2005-07-11 |  | 2008-06-01 | Central | Watson (Tower 55) | 1 | 138 |  | 370 | Reconductor 5.1 miles 954 kcmil ACSR from Central to Twr. 55 | J11 | MO | 5.1 |  | 100 |  |  |  | Planned | 1500300 | Eng | [5 empty] | Curt Stepanek |  | Y | N | Y
1411 | 2006-03-17 | BR | C-CSILL | Ameren | 720 | 2005-07-11 |  | 2008-12-01 | Page Substation | Replace 3-138 kV Breakers |  | 138 |  |  | replace existing 138 kV breakers | J10 | MO |  |  | 100 |  |  |  | Proposed | 539400 | Eng | 38335000 |  | date reflects more realistic schedule |  |  | Ameren - C Stepanek |  | Y | N | Y
58 | 2006-03-17 | BR | C-CSILL | Ameren | 151 | 2005-07-11 |  | 2009-06-01 | Dupo Ferry | Buck Knob | 1 | 138 |  | 240 | reconductor | J11 | IL | 22 |  | 100 |  |  |  | Proposed | 5170600 | Eng | [5 empty] | Curt Stepanek |  | Y | N | Y
1412 | 2006-03-17 | BR | C-CSILL | Ameren | 721 | 2005-07-11 |  | 2009-06-01 | Wildwood Sub. | Add 2-345 kV Breakers |  | 345 |  |  | install new 345 kV breakers | J11 | MO |  |  | 100 |  |  |  | Proposed | 1873200 | Eng | [5 empty] | Curt Stepanek |  | Y | N | Y
1932 | 2006-03-17 | BR | C-CSILL | Ameren | 1233 | 2006-03-17 |  | 2009-06-01 | Cahokia | Ashley | 1 | 138 |  | 318 | Replace bus conductor and retap CTs at Cahokia terminal | J11 | MO |  |  | 100 |  |  |  | Proposed | 116300 | Eng |  |  |  | 2006-03-17 | MTEP06 P2 | Curt Stepanek |  | Y | N | Y
1934 | 2006-03-17 | BR | C-CSILL | Ameren | 1235 | 2006-03-17 |  | 2009-06-01 | Fredericktown | AECI Fredericktown Tap | 1 | 161 |  | 250 | Increase ground clearance | K11 | MO | 12 |  | 100 |  |  |  | Proposed | 970500 | Eng | 8130600 |  |  | 2006-03-17 | MTEP06 P2 | Curt Stepanek |  | Y | N | Y
399 | 2006-03-17 | BR | C-CSILL | Ameren | 152 | 2005-07-11 |  | 2010-06-01 | Big River | Rockwood | 1 | 138 |  | 370 | new line | J11 | MO |  | 10 | 100 |  |  |  | Proposed | 12794000 | Eng |  |  | Distribution interconnection. ISD adjusted to meet need. |  |  | Ameren - C Stepanek |  | Y | N | Y
1936 | 2006-03-17 | BR | C-CSILL | Ameren | 1237 | 2006-03-17 |  | 2010-06-01 | Campbell | Euclid-Page | 1 | 138 |  | 415 | Rebuild dbl. ckt. 138 kV | J11 | MO | 5.25 |  | 100 |  |  |  | Proposed | 15254100 | Eng |  |  |  | 2006-03-17 | MTEP06 P2 | Curt Stepanek |  | Y | N | Y
1937 | 2006-03-17 | BR | C-CSILL | Ameren | 1238 | 2006-03-17 |  | 2010-06-01 | GM-Point Prairie 161 kV Line | AECI Enon Substation | 1 | 161 |  | 280 | Extend 1 mile of line to AECI Enon Substation | J10 | MO |  | 1 | 100 |  |  |  | Proposed | 1303500 | Eng |  |  |  | 2006-03-17 | MTEP06 P2 | Curt Stepanek |  | Y | N | Y
1940 | 2006-03-17 | BR | C-CSILL | Ameren | 1240 | 2006-03-17 |  | 2010-12-01 | Sioux | Huster | 3 | 138 |  | 370 | Reconductor 13 miles | J10 | MO | 13 |  | 100 |  |  |  | Proposed | 941050 | Eng |  |  |  | 2006-03-17 | MTEP06 P2 | Curt Stepanek |  | Y | N | Y
1939 | 2006-03-17 | BR | C-CSILL | Ameren | 1240 | 2006-03-17 |  | 2010-12-01 | Sioux | Huster | 1 | 138 |  | 370 | Reconductor 15 miles | J10 | MO | 15 |  | 100 |  |  |  | Proposed | 941050 | Eng | 31233700 |  |  | 2006-03-17 | MTEP06 P2 | Curt Stepanek |  | Y | N | Y
853 | 2006-07-05 | BR | C-CSILL | AmerenCILCO | 875 | 2005-07-11 |  | 2006-11-15 | Kickapoo | Mason City-Decatur |  | 138 |  | 155 | Replace 600 A terminal equipment with 1200 A at Kickapoo | K9 | IL |  |  | 100 |  |  |  | Planned | 156700 | Eng | [5 empty] | Ameren - J Sullivan |  | Y | N | Y
854 | 2006-03-17 | BR | C-CSILL | AmerenCILCO | 876 | 2005-07-11 |  | 2007-06-01 | Tazewell | Powerton | 1 | 345 |  | 1339 | Replace 2000 A terminal equipment at Tazewell with 3000 A | K9 | IL |  |  | 100 |  |  |  | Planned | 1042900 | Eng | [5 empty] | Curt Stepanek |  | Y | N | Y
386 | 2006-03-17 | BR | C-CSILL | AmerenCILCO | 141 | 2006-03-17 |  | 2009-06-01 | Duck Creek | Tazewell | 1 | 345 |  |  | convert bus duct to OH | K9 | IL | [5 empty] | 100 | Proposed | 119500 | Eng |  |  | Project need and timing under review |  |  | Ameren - C Stepanek |  | Y | N | Y
852 | 2006-03-17 | BR | C-CSILL | AmerenCILCO | 874 | 2005-07-11 |  | 2009-06-01 | East Springfield | Eastdale |  | 138 |  | 299 | Replace terminal equipment at East Springfield | K10 | IL |  |  | 100 |  |  |  | Proposed | 344300 | Eng | 463800 |  |  |  |  | Curt Stepanek |  | Y | N | Y
1417 | 2006-03-17 | BR | C-CSILL | AmerenIP | 724 | 2006-03-17 |  | 2006-12-01 | Rising | Bondville Rt. 10 | 1 | 138 |  | 266 | new 138 kV breaker at Rising and 3 miles new 138 kV line | K9 | IL |  | 3 | 100 |  |  |  | Planned | 2442500 | Eng | 2442500 |  | delays in obtaining permits |  |  | Ameren - C Stepanek |  | Y | N | Y
1425 | 2006-03-17 | BR | C-CSILL | AmerenIP | 732 | 2006-03-17 |  | 2007-06-01 | S. Bloomington | State Farm | 1 | 138 |  | 337 | Reconductor 1.3 miles 1272 kcmil ACSR | K9 | IL | 1.3 |  | 100 |  |  |  | Planned | 1172900 | Eng | [5 empty] | Ameren - C Stepanek |  | Y | N | Y
1429 | 2006-03-17 | BR | C-CSILL | AmerenIP | 736 | 2006-03-17 |  | 2007-06-01 | W. Tilton | Tilton Energy Center |  | 138 |  |  | new 138 kV breaker addition at W. Tilton | L9 | IL |  |  | 100 |  |  |  | Planned | 1709400 | Eng | [5 empty] | Ameren - C Stepanek |  | Y | N | Y
1431 | 2006-03-17 | BR | C-CSILL | AmerenIP | 738 | 2006-03-17 |  | 2007-06-01 | Line 1342C tap | Line 1342A | 1 | 138 |  | 280 | Line 1342A (structure 423 to 467A reconductor) | K9 | IL | 5.23 |  | 100 |  |  |  | Planned | 1994400 | Eng |  |  | date reflects more realistic work schedule |  |  | Ameren - C Stepanek |  | Y | N | Y
841 | 2006-03-17 | BR | C-CSILL | AmerenIP | 865 | 2006-03-17 |  | 2007-06-01 | Havana | Monmouth | 1 | 138 |  | 280 | Build new river crossing | J9 | IL |  | 0.44 | 100 |  |  |  | Planned | 223700 | Eng | [5 empty] | Curt Stepanek |  | Y | N | Y
842 | 2005-07-11 | BR | C-CSILL | AmerenIP | 866 | 2005-07-11 |  | 2007-06-01 | Latham 345/138 kV Substation | Mason City-Decatur Line 1342 | 1 | 138 |  | 160 | Install 138 kV breaker for 'in-out' taps to Line 1342, construct 0.38 mile 138 kV line | K9 | IL |  | 0.38 | 100 |  |  |  | Proposed | 1658000 | Planning MISO |  |  |  | 2005-07-11 | MTEP06 |  |  | Y | N | Y
845 | 2006-03-17 | BR | C-CSILL | AmerenIP | 869 | 2005-07-11 |  | 2007-06-01 | Sidney | Mira Tap | 1 | 138 |  | 280 | Reconductor 2 miles of 795 kcmil ACSR | L9 | IL | 2 |  | 100 |  |  |  | Planned | 693800 | Eng | 7452200 |  |  |  |  | Curt Stepanek |  | Y | N | Y
1667 | 2005-10-06 | SUB | C-CSILL | AmerenIP | 150 | 2006-03-17 | PS gen | 2008-06-01 | Prairie State | substation | 1 | 345 |  | 1793 | new switchyard (6 position, 4 lines, 2 units) | J11-K11 | IL |  |  |  | 100 |  |  | Planned |  |  | 101639970 |  | MISO submitted. Costs includes new transmission lines except river crossing |  |  |  | IP04 | Y | N | Y |  | Int?
1423 | 2006-03-17 | BR | C-CSILL | AmerenIP | 150 | 2006-03-17 | PS gen | 2008-06-01 | Line 4531 tap | Prairie State Power Plant | 2 | 345 |  | 1470 | 345 kV connection to new generation | K11 | IL |  | 7.5 |  | 100 |  |  | Planned | 2283900 |  |  |  | Project timing dependent on customer, permits, and right-of-way acquisition |  |  | Ameren - C Stepanek | IP04 | Y | N | Y |  | Int?
1424 | 2006-03-17 | BR | C-CSILL | AmerenIP | 150 | 2006-03-17 | PS gen | 2008-06-01 | Line 4541 tap | Prairie State Power Plant | 2 | 345 |  | 1470 | 345 kV connection to new generation | K11 | IL |  | 1.5 |  | 100 |  |  | Planned | 12991400 |  |  |  | Project timing dependent on customer, permits, and right-of-way acquisition |  |  | Ameren - C Stepanek | IP04 | Y | N | Y |  | Int?
1422 | 2006-03-17 | BR | C-CSILL | AmerenIP | 150 | 2006-03-17 | PS gen | 2008-06-01 | Baldwin | Rush Island | 1 | 345 |  | 1793 | 26 miles of new 345 kV line | J11-K11 | IL |  | 26 |  | 100 |  |  | Planned | 46149200 |  |  |  | Project timing dependent on customer, permits, and right-of-way acquisition |  |  | Ameren - C Stepanek | IP04 | Y | N | Y |  | Net?
1418 | 2006-03-17 | BR | C-CSILL | AmerenIP | 725 | 2006-03-17 | 725 | 2008-06-01 | N. LaSalle | Wedron Fox River | 1 | 138 |  | 266 | 2 CB at N LaSalle, 1 CB at Wedron Fox River Substation | K8 | IL |  | 25 | 100 |  |  |  | Planned | 20489370 | Eng |  |  | date reflects more realsitic permit and right-of-way acquisition activities |  |  | Ameren - C Stepanek |  | Y | N | Y
1419 | 2006-03-17 | BR | C-CSILL | AmerenIP | 726 | 2005-07-11 | 725 | 2008-06-01 | Ottawa | Wedron Fox River | 1 | 138 |  | 266 | 1 CB at Ottawa, new 138 kV line to Wedron Fox River Substation | K8 | IL |  | 8 | 100 |  |  |  | Planned | 8045400 | Eng |  |  | date reflects more realsitic permit and right-of-way acquisition activities |  |  | Ameren - C Stepanek |  | Y | N | Y
1421 | 2006-03-17 | BR | C-CSILL | AmerenIP | 728 | 2006-03-17 |  | 2008-06-01 | Wood River | Roxford L1502 | 1 | 138 |  | 382 | reconductor | K10 | IL | 4.36 |  | 100 |  |  |  | Planned | 5264900 | Eng |  |  | Schedule changed |  |  | Ameren - C Stepanek |  | Y | N | Y
846 | 2006-03-17 | BR | C-CSILL | AmerenIP | 870 | 2005-07-11 |  | 2008-06-01 | Sidney | Paxton | 1 | 138 |  | 399 | Reconductor 18 miles of 350 kcmil Cu | L9 | IL | 18 |  | 100 |  |  |  | Proposed | 5690300 | Eng | [5 empty] | Curt Stepanek |  | Y | N | Y
848 | 2006-03-17 | BR | C-CSILL | AmerenIP | 872 | 2005-07-11 |  | 2008-06-01 | Mahomet | Champaign | 1 | 138 |  | 240 | Reconductor 1.55 mile 477 kcmil ACSR from Mahomet Sub. To Twr. 29 | K9 | IL | 1.55 |  | 100 |  |  |  | Proposed | 725500 | Eng | [5 empty] | Curt Stepanek |  | Y | N | Y
1432 | 2006-03-17 | BR | C-CSILL | AmerenIP | 739 | 2006-03-17 |  | 2009-01-01 | Line 4561 Tap | Franklin County Power Plant | 1 | 345 |  |  | 345 kV connection (new ring bus) to new generation | K11 | IL |  |  |  | 100 |  |  | Proposed | 7108700 | Eng |  |  | customer has not moved forward in connection activities |  |  | Ameren - C Stepanek | IP17 | Y | N | Y |  | Int?
851 | 2006-03-17 | BR | C-CSILL | AmerenIP | 873 | 2005-07-11 |  | 2009-01-31 | Baldwin | Turkey Hill | 1 | 345 |  | 1195 | Replace 345 kV breakers at Baldwin terminal | K11 | IL |  |  |  | 100 |  |  | Planned | 4242100 | Eng | [5 empty] | Curt Stepanek |  | Y | N | Y
850 | 2006-03-17 | BR | C-CSILL | AmerenIP | 873 | 2005-07-11 |  | 2009-01-31 | Baldwin | Stallings | 1 | 345 |  | 1195 | Replace 345 kV breakers at Baldwin terminal | K11 | IL |  |  |  | 100 |  |  | Planned | 4242100 | Eng | [5 empty] | Curt Stepanek |  | Y | N | Y
849 | 2006-03-17 | BR | C-CSILL | AmerenIP | 873 | 2005-07-11 |  | 2009-01-31 | Baldwin | W. Mt. Vernon | 1 | 345 |  | 1195 | Replace 345 kV breakers at Baldwin terminal | K11 | IL |  |  |  | 100 |  |  | Planned | 4242100 | Eng | [5 empty] | Curt Stepanek |  | Y | N | Y
1427 | 2006-03-17 | BR | C-CSILL | AmerenIP | 734 | 2006-03-17 |  | 2009-06-01 | Line 1364 (new tap) | Washington Street Sub | 2 | 138 |  | 266 | install ring bus and split S.Bloomington to Raab Rd. | K9 | IL |  | 0.17 | 100 |  |  |  | Proposed | 4066500 | Eng |  |  | Project need and timing under review |  |  | Ameren - C Stepanek | A109 | Y | N | Y |  |  | Y
1428 | 2006-03-17 | BR | C-CSILL | AmerenIP | 734 | 2006-03-17 |  | 2009-06-01 | Washington St. Line 1364 | S. Bloomington | 1 | 138 |  | 266 | reconductor Line 1364 from S. Bloomington to Tower 512 | K9 | IL | 3.3 |  | 100 |  |  |  | Proposed | 1693800 | Eng |  |  | Project need and timing under review |  |  | Ameren - C Stepanek |  | Y | N | Y
1430 | 2006-03-17 | BR | C-CSILL | AmerenIP | 737 | 2006-03-17 |  | 2009-06-01 | B luff City | W. Salem |  | 138 |  |  | new 138 kV breaker addition at Bluff City | K10 | IL |  |  | 100 |  |  |  | Proposed | 1756400 | Eng |  |  | distribution project need and timing under review |  |  | Ameren - C Stepanek |  | Y | N | Y
1933 | 2006-03-17 | BR | C-CSILL | AmerenIP | 1234 | 2006-03-17 |  | 2009-06-01 | Havana, South | Mason City, West | 1 | 138 |  | 155 | Increase ground clearance on 18.4 miles | J9 | IL | 18.4 |  | 100 |  |  |  | Proposed | 642300 | Eng |  |  |  | 2006-03-17 | MTEP06 P2 | Curt Stepanek |  | Y | N | Y
1935 | 2006-03-17 | BR | C-CSILL | AmerenIP | 1236 | 2006-03-17 |  | 2009-06-01 | Stallings | Prairie State Power Plant | 1 | 345 |  | 1297 | Replace 2000 A terminal equipment with 3000 A equipment at Stallings | K11 | IL |  |  |  | 100 |  |  | Proposed |  |  | 27994000 |  |  | 2006-03-17 | MTEP06 P2 | Curt Stepanek |  | Y | N | Y
1941 | 2006-03-17 | BR | C-CSILL | AmerenIP |  |  |  | 2010-06-01 | Pana, North | Decatur Rt. 51 L1462 | 1 | 138 |  | 280 | Replace 1200 A terminal equipment with 1600 A equipment at Pana | K10 | IL |  |  | 100 |  |  |  | Proposed |  |  |  |  | No project | 2006-03-17 | MTEP06 P2 | Curt Stepanek |  | Y | N | Y
1938 | 2006-03-17 | BR | C-CSILL | AmerenIP | 1239 | 2006-03-17 |  | 2010-06-01 | Normal East | Brokaw | 1 | 138 |  | 280 | Replace 600 A terminal equipment to 1200 A at Normal, East | K9 | IL |  |  | 100 |  |  |  | Proposed | [5 empty] | 2006-03-17 | MTEP06 P2 | Curt Stepanek |  | Y | N | Y
1747 | 2005-11-18 | GEN | Central | ATC | 1097 | 2005-11-18 |  | 2005-03-07 |  | generator |  |  |  | 105 | new generator |  | WI |  |  |  | 100 |  |  | Under Construction |  |  |  |  | 39180(CT), 39181(CT), 39182(ST) |  |  |  | G096 | Y | N | Y |  | Generator
1762 | 2005-11-18 | GEN | Central | ATC | 1112 | 2005-11-18 |  | 2005-03-07 |  | generator |  |  |  | 45 | new generator |  | WI |  |  |  | 100 |  |  | Under Construction | [8 empty] | G160 | Y | N | Y |  | Generator
1725 | 2005-11-18 | GEN | Central | ATC | 1075 | 2005-11-18 |  | 2005-06-01 |  | generator |  |  |  | 600 | new generator |  | WI |  |  |  | 100 |  |  | Under Construction |  |  |  |  | 39557 (CT), 39558 (CT), 39559 (ST) |  |  |  | G044 | Y | N | Y |  | Generator
1748 | 2005-11-18 | GEN | Central | ATC | 1098 | 2005-11-18 |  | 2005-06-01 |  | generator | 1 |  |  | 370 | new generator |  | WI |  |  |  | 100 |  |  | Under Construction |  |  |  |  | 39434 |  |  |  | G103 | Y | N | Y |  | Generator
1698 | 2005-11-18 | GEN | Central | ATC | 1048 | 2005-11-18 |  | 2005-07-01 | Port Washington | generator |  |  |  | 1000 | new generator |  | WI |  |  |  | 100 |  |  | Under Construction |  |  |  |  | 39453 (GT), 39455 (GT), 39457 (GT), 39459 (GT), 39454 (ST), 39458 (ST) |  |  |  | G014 | Y | N | Y |  | Generator
1779 | 2005-11-18 | GEN | Central | ATC | 1129 | 2005-11-18 |  | 2005-09-01 |  | generator | 7 |  |  | 55 | new generator |  | WI |  |  |  | 100 |  |  | Under Construction |  |  |  |  | 39653 |  |  |  | G240 | Y | N | Y |  | Generator
1824 | 2005-11-18 | GEN | Central | ATC | 1174 | 2005-11-18 |  | 2006-05-01 | Navitas Energy | generator | 6 |  |  | 80 | new generator |  | WI |  |  |  | 100 |  |  | Planned |  |  |  |  | 61665 |  |  |  | G353 | Y | N | Y |  | Generator
1825 | 2005-11-18 | GEN | Central | ATC | 1175 | 2005-11-18 |  | 2006-05-01 | Navitas Energy | generator | 6 |  |  | 80 | new generator |  | WI |  |  |  | 100 |  |  | Planned |  |  |  |  | 61665 |  |  |  | G354 | Y | N | Y |  | Generator
1757 | 2005-11-18 | GEN | Central | ATC | 1107 | 2005-11-18 |  | 2007-06-01 |  | generator | 4 |  |  | 550 | new generator |  | WI |  |  |  | 100 |  |  | Planned |  |  |  |  | 39662 |  |  |  | G144 | Y | N | Y |  | Generator
1745 | 2005-11-18 | GEN | Central | ATC | 1095 | 2005-11-18 |  | 2008-05-01 |  | generator |  |  |  | 200 | new generator |  | WI |  |  |  | 100 |  |  | Under Construction |  |  |  |  | 39453 (GT), 39455 (GT), 39457 (GT), 39459 (GT), 39454 (ST), 39458 (ST) |  |  |  | G093 | Y | N | Y |  | Generator
1727 | 2005-11-18 | GEN | Central | ATC | 1077 | 2005-11-18 |  | 2009-01-01 |  | generator |  |  |  | 1950 | new generator |  | WI |  |  |  | 100 |  |  | Planned |  |  |  |  | 39389, 39390 |  |  |  | G051 | Y | N | Y |  | Generator
1733 | 2005-11-18 | GEN | Central | ATC | 1083 | 2005-11-18 |  |  |  | generator | 46DE |  |  | 90 | new generator |  | WI |  |  |  | 100 |  |  | Under Construction |  |  |  |  | 39651 |  |  |  | G063 | Y | N | Y |  | Generator
1963 | 2006-07-05 | SUB | C-WUMS | ATC LLC |  |  | no Proj | 2006-06-01 | ER Muni |  |  | 115 |  |  | Construct new SS adjacent to the Cranberry 115-kV SS |  | WI | [6 empty] | Under Construction |  |  |  |  | Where is this interconnected? | 2006-04-05 | MTEP06 | ATC - Wenchun Zhu |  | Y | N | Y
127 | 2006-07-05 | BR | C-WUMS | ATC LLC | 2 | 2005-07-11 | 1 | 2006-06-01 | Northpoint | Dewey Tap |  | 115 |  | 241 | Phase I increase clearance/ Phase II reconductor 12/31/07 | K6 | WI | 8.2 |  | 50 |  | 25 | 25 | Planned | 1100000 | Eng |  |  | Phase I complete, Phase II scheduled for late 2007 |  |  | ATC - Wenchun Zhu | G144 | Y | N | Y |  | Network
121 | 2006-07-05 | BR | C-WUMS | ATC LLC | 2 | 2005-07-11 | 1 | 2006-06-01 | Dewey Tap | Weston |  | 115 |  | 241 | Phase I increase clearance/ Phase II reconductor 12/31/07 | K6 | WI | 15.4 |  | 50 |  | 25 | 25 | Planned | 4400000 | Eng |  |  | Phase I complete, Phase II scheduled for late 2007 |  |  | ATC - Wenchun Zhu | G144 | Y | N | Y |  | Newtork
439 | 2005-07-11 | BR | C-WUMS | ATC LLC | 171 | 2005-07-11 |  | 2006-06-01 | Weston | Kelly |  | 115 |  | 239 | uprate clearances to 300F | K6 | WI | 6.4 |  | 50 |  | 25 | 25 | Planned | 1000000 | Eng | [6 empty] | A105, F006, F009 | Y | N | Y |  |  | Y
2061 | 2006-07-05 | DV | C-WUMS | ATC LLC | 432 | 2005-07-11 |  | 2006-11-01 | Summit Lake | Capacitor bank |  | 115 |  | 5.6 Mvar | upgrade existing 11.3 to 16.9 Mvar | K5 | WI | [5 empty] | 100 | Planned | 1000000 | Eng |  |  | Construction Delay |  |  | ATC - Wenchun Zhu |  | Y | N | Y
133 | 2006-07-05 | BR | C-WUMS | ATC LLC | 15 | 2006-07-05 | 9 | 2006-12-01 | Stiles | Amberg (rebuild) |  | 138 |  | 345 | rebuild | K6 | WI | 44.1 |  | 60 |  | 20 | 20 | Under Construction | 7500000 | Eng |  | FTR ATC20 | Construction Delay |  |  | ATC - Wenchun Zhu | A105, F006 | Y | N | Y | ATC zone 4 |  | Y
120 | 2006-07-05 | BR | C-WUMS | ATC LLC | 15 | 2006-07-05 | 9 | 2006-12-01 | Crivitz | Stiles (rebuild) |  | 138 |  | 345 | rebuild | K6 | WI | 24.1 |  | 60 |  | 20 | 20 | Under Construction | 22900000 | Eng |  | FTR ATC22 | Construction Delay |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 4
436 | 2006-07-05 | BR | C-WUMS | ATC LLC | 168 | 2005-07-11 |  | 2006-12-31 | Werner West | transformer |  | 345 | 138 | 500 |  | K6 | WI |  |  | 33 |  | 34 | 33 | Under Construction | 14300000 | Eng |  |  | Combination of 1. Delays in obtaining regulatory approvals 2. Delays in obtaining real estate. A project for uprating North Appleton-Ellington 138 kV line is planned for May 2006 to address the potential line overload due to the delay of the Werner West 3 |  |  | ATC - Wenchun Zhu | A013,A105,A120,A153,A163, A191,F005,F006,F007,F009 | Y | N | Y |  |  | Y
108 | 2006-07-05 | BR | C-WUMS | ATC LLC | 62 | 2005-11-18 | 44 | 2007-03-01 | Stratford | McMillan |  | 115 |  | 135 |  | J6 | WI | 10 |  | 60 |  | 20 | 20 | Planned | 1750000 | Eng |  | FTR ATC31 | construction/third party delay to March 2007 |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 1
2082 | 2006-07-05 | DV | C-WUMS | ATC LLC | 446 | 2005-07-11 |  | 2007-04-30 | Rubicon | Capacitor bank |  | 138 |  | 32 Mvar | was Hartford | K7 | WI | [5 empty] | 100 | Planned | 750000 | Eng |  |  | Construction Delay |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 5
119 | 2006-07-05 | BR | C-WUMS | ATC LLC | 21 | 2005-07-11 | 10 | 2007-06-01 | Venus | Metonga (was Crandon) |  | 115 |  | 175 |  | K5 | WI |  | 14 | 100 |  |  |  | Under Construction | 8000000 | Eng |  | FTR ATC38 |  |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 1
132 | 2006-04-05 | BR | C-WUMS | ATC LLC | 22 | 2005-11-18 | 11 | 2007-06-01 | Sprecher | Reiner (conversion to 138 kV) |  | 138 |  | 366 | conversion to 138 | K7 | WI | 10 |  | 75 |  |  | 25 | Planned | 1250000 | Eng | [5 empty] | Wenchun Zhu | A130 | Y | N | Y | ATC zone 3 |  | Y
131 | 2006-04-05 | BR | C-WUMS | ATC LLC | 22 | 2005-11-18 | 11 | 2007-06-01 | Reiner | Sycamore (conversion to 138 kV) |  | 138 |  | 366 | conversion to 138 | K7 | WI | 7 |  | 75 |  |  | 25 | Planned | 1250000 | Eng | [5 empty] | Wenchun Zhu | A130 | Y | N | Y | ATC zone 3 |  | Y
123 | 2006-04-05 | BR | C-WUMS | ATC LLC | 22 | 2005-11-18 | 11 | 2007-06-01 | Femrite | Sprecher (new 138 kV) | 1 | 138 |  | 348 | new 138 kV line | K7 | WI |  | 5 | 50 |  | 50 |  | Planned | 8100000 | Eng | [5 empty] | Wenchun Zhu | A130 | Y | N | Y | ATC zone 3 |  | Y
87 | 2006-04-05 | BR | C-WUMS | ATC LLC | 64 | 2005-07-11 | 46 | 2007-06-01 | McFarland | Femrite (conversion to 138 kV) |  | 138 |  | 438 | conversion to 138 | K7 | WI | 2.1 |  | 75 |  |  | 25 | Planned | 1000000 | Eng | [5 empty] | Wenchun Zhu | A130 | Y | N | Y | ATC zone 3 |  | Y
86 | 2006-04-05 | BR | C-WUMS | ATC LLC | 64 | 2005-07-11 | 46 | 2007-06-01 | Kegonsa | McFarland (conversion to 138 kV) |  | 138 |  | 348 | conversion to 138 | K7 | WI | 3.7 |  | 75 |  |  | 25 | Planned | 2410000 | Eng | [5 empty] | Wenchun Zhu | A130 | Y | N | Y | ATC zone 3 |  | Y
463 | 2006-07-05 | BR | C-WUMS | ATC LLC | 175 | 2005-07-11 |  | 2007-06-01 | Ellinwood | Sunset Point |  | 138 |  | 289 MVA SE |  | K6 | WI | 3.6 |  | 100 |  |  |  | Proposed | 2500000 | Eng |  |  | Further study has found 2007 is the appropriate in service date. |  |  | ATC - Wenchun Zhu |  | Y | N | Y
891 | 2006-07-05 | BR | C-WUMS | ATC LLC | 333 | 2006-03-16 | newgrp12 | 2007-06-01 | Mackinac | Substation relocation |  | 138 |  |  | Straits substation rename/relocation | M5 | MI |  |  | 50 |  |  | 50 | Proposed | 5800000 | Eng |  |  | ATC Provisional status | 2005-07-11 | MTEP06 | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 2
458 | 2006-04-05 | BR | C-WUMS | ATC LLC | 350 | 2005-07-11 | newgrp3 | 2007-06-01 | Weston | Sherman St |  | 115 |  | 239 | rebuild | J6 | WI | 0.2 |  | 50 |  | 25 | 25 | Planned | 250000 | Eng | [5 empty] | Wenchun Zhu | A105, A122, F006 | Y | N | Y | ATC zone 1 |  | Y
1247 | 2006-04-05 | BR | C-WUMS | ATC LLC | 350 | 2005-07-11 |  | 2007-06-01 | Gardner Park (was Weston) | Hilltop |  | 115 |  | 285 | new line | K6 | WI | 2.4 |  | 50 |  | 25 | 25 | Planned | 3750000 | Eng | [5 empty] | Wenchun Zhu | A122 | Y | N | Y | ATC zone 1 |  | Y
459 | 2006-04-05 | BR | C-WUMS | ATC LLC | 350 | 2005-07-11 | newgrp3 | 2007-06-01 | Sherman St | Hilltop |  | 115 |  | 239 | rebuild | J6 | WI | 6.9 |  | 50 |  | 25 | 25 | Planned | 3750000 | Eng | [5 empty] | Wenchun Zhu | A105, A122, F006 | Y | N | Y | ATC zone 1 |  | Y
2062 | 2006-07-05 | DV | C-WUMS | ATC LLC | 433 | 2005-07-11 |  | 2007-06-01 | Wautoma | Capacitor bank |  | 138 |  | 2x24.5 Mvar |  | K6 | WI | [5 empty] | 100 | Planned | 1200000 | Eng | [5 empty] | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 1
1244 | 2006-07-05 | BR | C-WUMS | ATC LLC | 566 | 2005-07-11 |  | 2007-06-01 | Plymouth | Forest Junction/Charter Steel | 1 | 138 |  | 277 |  | K6 | WI |  | 1.3 | 100 |  |  |  | Proposed | 2500000 | Eng | [5 empty] | ATC - Wenchun Zhu |  | Y | N | Y
1245 | 2006-07-05 | BR | C-WUMS | ATC LLC | 567 | 2005-07-11 | 567 | 2007-06-01 | North Appleton | Lawn Road | 1 | 138 |  | 287 |  | K6 | WI | 15 |  |  |  | 100 |  | Proposed | 300000 | Eng | [5 empty] | ATC - Wenchun Zhu |  | Y | N | Y
1246 | 2006-07-05 | BR | C-WUMS | ATC LLC | 567 | 2005-07-11 | 567 | 2007-06-01 | Lawn Road | White Clay | 1 | 138 |  | 287 |  | K6 | WI | 15 |  |  |  | 100 |  | Proposed | 300000 | Eng | [5 empty] | ATC - Wenchun Zhu |  | Y | N | Y
882 | 2005-07-11 | DV | C-WUMS | ATC LLC | 882 | 2006-07-05 | new105 | 2007-06-01 | Ontonagon | Capacitor bank |  | 138 |  | 16.32 Mvar | add 2x8.16 Mvar Capacitors |  | MI |  |  | 100 |  |  | 100 | Proposed | 1200000 | Eng |  |  |  | 2005-07-11 | MTEP06 |  |  | Y | N | Y
889 | 2006-07-05 | BR | C-WUMS | ATC LLC | 889 | 2005-07-11 | new112 | 2007-10-01 | Aspen | Substation relocation |  | 69 |  |  | Brule substation rename/relocation | K5 | MI |  |  | 50 |  |  | 50 | Planned | 5700000 | Eng |  |  |  | 2005-07-11 | MTEP06 | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 2
1868 | 2006-07-05 | BR | West | ATC LLC |  |  | no Proj | 2008-01-01 | Waunakee | Westport - Pheasant Branch |  | 69 |  | 95 MVA SE | Uprate of Waunakee-Westport-Pheasant Branch 69 kV line |  | WI |  |  |  |  | 100 |  | Planned |  |  |  |  | Submitted by MISO |  |  | ATC - Wenchun Zhu | A130, A174 | Y | N | Y |  |  | Y
447 | 2005-11-28 | BR | C-WUMS | ATC LLC | 352 | 2006-03-16 | newgrp4 | 2008-01-01 | Conover 138-115 kV | transformer | 1 | 138 | 115 | 150 | cost includes 138/115 and 138/69 transformers at Conover | K5 | WI |  |  | 50 |  | 25 | 25 | Planned | 18500000 | Eng |  |  | Transformer will be at Convoer instead of Cranberry due to space limitations |  |  |  | A105, A215, F006 | Y | N | Y |  |  | Y
446 | 2005-11-28 | BR | C-WUMS | ATC LLC | 352 | 2006-03-16 | newgrp4 | 2008-01-01 | Cranberry | Conover | 1 | 115 |  | 244 | new line | K5 | WI |  | 14 | 50 |  | 25 | 25 | Planned | 17000000 | Eng |  |  | Line to be constructed for 138kV but to be operated at 115 |  |  |  | A105, A215, F006 | Y | N | Y |  |  | Y
1865 | 2006-07-05 | BR | West | ATC LLC |  |  | no Proj | 2008-06-01 | N. Madison | ABS -Yahara |  | 138 |  |  | Uprate of N.Madison-ABS 138kV and ABS-Yahara 138kV lines |  | WI |  |  |  |  | 100 |  | Planned |  |  |  |  | Submitted by MISO, typo not needed until 2008 |  |  | ATC - Wenchun Zhu | A130, A174 | Y | N | Y |  |  | Y
855 | 2006-04-05 | DV | C-WUMS | ATC LLC | 1 | 2005-07-11 | 1 | 2008-06-01 | Stone Lake | Inductor |  | 345 |  | 75 Mvar |  | J6 | WI | [5 empty] | 100 | Planned | 0 | Eng |  |  |  | 2005-07-11 | MTEP06 | Wenchun Zhu |  | Y | N | Y | ATC zone 1
1453 | 2006-03-16 | BR | C-WUMS | ATC LLC | 1 | 2005-07-11 | 1 | 2008-06-01 | Cornell (4.5 ohm reactor) | Fiebrantz |  | 138 |  |  |  | K6 | WI | [5 empty] | 100 | Proposed | 800000 | Eng |  |  | We are in the process of evaluating an operating guide that will have the same effect without the cost of a reactor. |  |  | ATC - Paul Hesse | A130 | Y | N | Y |  |  | Y
3099 | 2005-07-11 | DV | C-WUMS | ATC LLC | 1 | 2005-07-11 | 1 | 2008-06-01 | Stone Lake | Capacitor |  | 345 |  | 75 Mvar |  | J6 | WI | [5 empty] | 100 | Planned | 0 | Eng | [7 empty] | Y | N | Y
2064 | 2005-07-11 | DV | C-WUMS | ATC LLC | 1 | 2005-07-11 | 1 | 2008-06-01 | Arpin | Capacitor bank |  | 138 |  | 50 Mvar |  | J6 | WI | [5 empty] | 100 | Planned | 1021496 | Eng | [7 empty] | Y | N | Y
125 | 2006-04-05 | BR | C-WUMS | ATC LLC | 101 | 2005-07-11 | 82 | 2008-06-01 | Kelly | Whitcomb |  | 115 |  | 121 | uprate clearances to 300F | K6 | WI | 24.3 |  | 50 |  | 25 | 25 | Planned | 1900000 | Eng | [5 empty] | Wenchun Zhu | A105, F006 | Y | N | Y | ATC zone 1 |  | Y
467 | 2005-07-11 | BR | C-WUMS | ATC LLC | 102 | 2006-03-16 | 83 | 2008-06-01 | Pleasant Valley | Saukville |  | 138 |  | 290 | reconductor | K7 | WI | 12 |  |  | 25 |  | 75 | Planned | 3000000 | Eng | [6 empty] | G014, G093, A130 | Y | N | Y |  | Network | Y
468 | 2005-07-11 | BR | C-WUMS | ATC LLC | 102 | 2006-03-16 | 83 | 2008-06-01 | Pleasant Valley | St. Lawrence |  | 138 |  | 290 | reconductor | K7 | WI | 7 |  |  | 25 |  | 75 | Planned | 3100000 | Eng | [6 empty] | G014, G093, A130 | Y | N | Y |  | Network | Y
429 | 2006-07-05 | BR | C-WUMS | ATC LLC | 339 | 2005-07-11 | newgrp15 | 2008-06-01 | Lakehead Cambridge | Jefferson |  | 138 |  | 348 | uprate | K7 | WI |  |  | 25 |  | 75 |  | Planned | 150000 | Eng |  | FTR ATC41 | Regulatory/Construction Delay |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 3
450 | 2006-07-05 | BR | C-WUMS | ATC LLC | 339 | 2005-07-11 | newgrp15 | 2008-06-01 | Lake Mills (provisional) | Stonybrook |  | 138 |  | 290 | construct new | K7 | WI |  | 6 | 100 |  |  |  | Planned | 9850000 | Eng |  |  | Regulatory/Construction Delay |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 3
449 | 2006-07-05 | BR | C-WUMS | ATC LLC | 339 | 2005-07-11 | newgrp15 | 2008-06-01 | Jefferson | Lake Mills (provisional) |  | 138 |  | 290 | construct new | K7 | WI |  | 6 | 100 |  |  |  | Planned | 9850000 | Eng |  |  | Regulatory/Construction Delay |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 3
892 | 2006-07-05 | BR | C-WUMS | ATC LLC | 339 | 2005-07-11 | newgrp15 | 2008-06-01 | Boxelder | Stonybrook |  | 138 |  | 287 | uprate | K7 | WI |  |  | 50 |  | 50 |  | Planned | 200000 | Eng | Delayed Need |  |  | 2005-07-11 | MTEP06 | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 3
434 | 2006-07-05 | BR | C-WUMS | ATC LLC | 339 | 2005-07-11 | newgrp15 | 2008-06-01 | Rockdale | Boxelder | 1 | 138 |  | 383 | uprate | K7 | WI |  |  | 50 |  | 50 |  | Planned | 200000 | Eng |  | FTR ATC40 | Regulatory/Construction Delay |  |  | ATC - Wenchun Zhu |  | Y | N | N
433 | 2006-07-05 | BR | C-WUMS | ATC LLC | 339 | 2005-07-11 | newgrp15 | 2008-06-01 | Rockdale | Lakehead Cambridge |  | 138 |  | 287 | uprate | K7 | WI |  |  | 25 |  | 75 |  | Planned | 200000 | Eng |  | FTR ATC37 | Regulatory/Construction Delay |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 3
597 | 2006-07-05 | BR | C-WUMS | ATC LLC | 347 | 2005-07-11 | newgrp21 | 2008-06-01 | Rubicon | Hustisford |  | 138 |  | 348 |  | K7 | WI |  | 5 | 100 |  |  |  | Proposed | 4800000 | Eng | [5 empty] | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 3
598 | 2006-07-05 | BR | C-WUMS | ATC LLC | 347 | 2005-07-11 | newgrp21 | 2008-06-01 | Hustisford | Hubbard (convert) |  | 138 |  | 348 | convert | K7 | WI | 8 |  | 100 |  |  |  | Proposed | 2400000 | Eng |  |  | Horicon to Hubbard |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 3
898 | 2006-07-05 | BR | C-WUMS | ATC LLC | 544 | 2005-07-11 | p2-104 | 2008-06-01 | Bluemound | Capacitor bank |  | 138 |  | 200 Mvar |  | L7 | WI |  |  | 100 |  |  |  | Proposed | 3300000 | Eng |  |  | ATC Provisional status | 2005-07-11 | MTEP06 | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 5
1242 | 2006-04-05 | BR | C-WUMS | ATC LLC | 551 | 2005-07-11 |  | 2008-06-01 | Stone Lake 345-161kV | transformer | 1 | 345 | 161 | 300 |  | J6 | WI |  |  | 50 |  | 25 | 25 | Planned | 8100000 | Eng |  |  | Temp sub will be in service 12/06; Permanent sub will be in service 6/08 |  |  | Wenchun Zhu |  | Y | N | Y | ATC zone 1
1992 | 2006-07-05 | LN | C-WUMS | ATC LLC | 571 | 2005-07-11 |  | 2008-06-01 | North Madison | Huiskamp | 1 | 138 |  | 481 MVA SE |  |  | WI | [6 empty] | Proposed | [5 empty] | 2006-07-05 |  | ATC - Wenchun Zhu |  | Y | N | Y
1261 | 2006-07-05 | BR | C-WUMS | ATC LLC | 571 | 2005-07-11 |  | 2008-06-01 | North Madison | Waunakee | 1 | 138 |  | 480 |  | K7 | WI |  | 5 | 100 |  |  |  | Planned | 10100000 | Eng | Replaced by North Madison-Huiskamp |  |  |  |  | ATC - Wenchun Zhu | A130, A174 | Y | N | Y |  |  | Y
1263 | 2006-07-05 | BR | C-WUMS | ATC LLC | 572 | 2005-07-11 |  | 2008-06-01 | Menominee | Bay de Noc | 1 | 138 |  | 345 |  | K5 | WI |  | 0.45 | 100 |  |  |  | Proposed | 1000000 | Eng |  |  | ATC Provisional status |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 4
1262 | 2006-07-05 | BR | C-WUMS | ATC LLC | 572 | 2005-07-11 |  | 2008-06-01 | Ingalls | Bay de Noc | 1 | 138 |  | 345 |  | K5 | WI |  | 0.45 | 100 |  |  |  | Proposed | 1000000 | Eng |  |  | Provisional. Scope change. A 2nd 138 kV circuit is not being added |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 4
1264 | 2006-07-05 | BR | C-WUMS | ATC LLC | 572 | 2005-07-11 |  | 2008-06-01 | Menominee 138/69 | transformer | 1 | 138 | 69 |  |  |  | WI |  |  | 100 |  |  |  | Proposed | 1915000 | Planning MISO |  |  | ATC Provisional status | 2004-09-27 |  | ATC - Wenchun Zhu |  | Y | N | Y
879 | 2005-07-11 | BR | C-WUMS | ATC LLC | 880 | 2005-07-11 | new103 | 2008-06-01 | North Appleton | Lost Dauphin | 1 | 138 |  | 288 | uprate 138 kV line | K5 | WI | 12 |  | 50 |  |  | 50 | Proposed | 1600000 | Eng |  |  |  | 2005-07-11 | MTEP06 |  | A191, A215 | Y | N | Y |  |  | Y
878 | 2005-07-11 | BR | C-WUMS | ATC LLC | 880 | 2005-07-11 | new103 | 2008-06-01 | North Appleton | Mason Street | 1 | 138 |  | 229 | uprate 138 kV line | K5 | WI | 21 |  | 50 |  |  | 50 | Proposed | 1700000 | Eng |  |  |  | 2005-07-11 | MTEP06 |  | A191, A215 | Y | N | Y |  |  | Y
886 | 2006-07-05 | SUB | C-WUMS | ATC LLC | 886 | 2005-07-11 | new109 | 2008-06-01 | North Lake | Substation relocation |  | 138 |  |  | Cedar substation rename/relocation | K4 | MI |  |  | 50 |  |  | 50 | Planned | 7300000 | Eng |  |  |  | 2005-07-11 | MTEP06 | ATC - Wenchun Zhu |  | Y | N | Y
888 | 2005-07-11 | BR | C-WUMS | ATC LLC | 888 | 2005-07-11 | new111 | 2008-06-01 | Plains 345-138 kV | transformer | 2 | 345 | 138 | 500 | second 500 MVA transformer | K5 | MI | [5 empty] | 100 | Proposed | 5400000 | Eng |  |  |  | 2005-07-11 | MTEP06 |  |  | Y | N | Y
135 | 2006-07-05 | BR | N-NM | ATC LLC | 1 | 2005-07-11 | 1 | 2008-06-30 | Arrowhead | Gardner Park | 1 | 345 |  | 750 | Gardner Park-Stone Lake 2006, Stone Lake-Arrowhead 2008 | I4 | WI |  | 220 | 50 |  | 25 | 25 | Under Construction | 364645722.88 | Eng |  |  | Summer rating is safe contingent PV nose limit per George Sweezy 1/20/06. line thermal 1200 MVA |  |  | ATC - Wenchun Zhu | A191, F009 | Y | N | Y |  |  | Y
445 | 2006-04-05 | BR | C-WUMS | ATC LLC | 352 | 2006-03-16 | newgrp4 | 2008-07-31 | Conover | Iron Grove | 1 | 138 |  | 290 | convert 69 to 138 kV | K5 | MI/WI | 73 |  | 50 |  | 25 | 25 | Planned | 69100000 | Eng |  |  | Construction schedule limitations |  |  | Wenchun Zhu | A105, A215, F006 | Y | N | Y | ATC zone 2 |  | Y
474 | 2006-07-05 | BR | C-WUMS | ATC LLC | 333 | 2006-03-16 | newgrp12 | 2009-05-01 | Hiawatha | Indian Lake (convert double circuit 138 kV from 69 kV operation to 138 kV o | 2 | 138 |  | 279 | rebuild in 2006 and convert in 2009 | L5 | MI | 40 |  | 30 |  | 30 | 40 | Proposed | 200000 | Eng |  |  | ATC Provisional status |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 2
596 | 2006-07-05 | BR | C-WUMS | ATC LLC | 333 | 2006-03-16 | newgrp12 | 2009-05-01 | Hiawatha | Indian Lake (string second 138 kV circuit) | 2 | 138 |  | 279 | string 2nd 138 kV circuit | L5 | WI |  | 40 | 30 |  | 30 | 40 | Proposed | 200000 | Eng |  |  | Provisional. 2nd circuit strung but terminal have not been constructed |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 2
862 | 2005-07-11 | SUB | C-WUMS | ATC LLC | 177 | 2006-03-16 | 155 | 2009-06-01 | Central Wisconsin | new substation |  | 345 |  |  | new substation | K6 | WI | [6 empty] | Planned | 12200000 | Eng |  |  |  | 2005-07-11 | MTEP06 |  | G144, F009 | Y | N | Y |  | Network | Y
1259 | 2006-07-05 | BR | C-WUMS | ATC LLC | 570 | 2005-07-11 |  | 2009-06-01 | North Shore | Bristol | 1 | 138 |  | 381 |  | K7 | WI |  |  | 100 |  |  |  | Planned | 1610612 | Eng |  |  | Regulatory Filing delays |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 3
1260 | 2006-07-05 | BR | C-WUMS | ATC LLC | 570 | 2005-07-11 |  | 2009-06-01 | Bristol | Elkhorn | 1 | 138 |  | 292 |  | K7 | WI |  |  | 100 |  |  |  | Planned | 3410708 | Eng |  |  | Regulatory Filing delays |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 3
1258 | 2006-07-05 | BR | C-WUMS | ATC LLC | 570 | 2005-07-11 |  | 2009-06-01 | Southwest Delavan | North Shore | 1 | 138 |  | 381 |  | K7 | WI |  |  | 100 |  |  |  | Planned | 3410708 | Eng |  |  | Regulatory Filing delays |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 3
1257 | 2006-07-05 | BR | C-WUMS | ATC LLC | 570 | 2005-07-11 |  | 2009-06-01 | West Darien | Southwest Delavan | 1 | 138 |  | 381 |  | K7 | WI |  |  | 100 |  |  |  | Planned | 1610612 | Eng |  |  | Regulatory Filing delays |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 3
1256 | 2006-07-05 | BR | C-WUMS | ATC LLC | 570 | 2005-07-11 |  | 2009-06-01 | Bradford RCEC | West Darien | 1 | 138 |  | 381 |  | K7 | WI |  |  | 100 |  |  |  | Planned | 3410708 | Eng |  |  | Regulatory Filing delays |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 3
1255 | 2006-07-05 | BR | C-WUMS | ATC LLC | 570 | 2005-07-11 |  | 2009-06-01 | La Prairie RCEC | Bradford RCEC | 1 | 138 |  | 381 |  | K7 | WI |  |  | 100 |  |  |  | Planned | 1610612 | Eng |  |  | Regulatory Filing delays |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 3
871 | 2006-07-05 | BR | C-WUMS | ATC LLC | 877 | 2006-03-16 | new100 | 2009-06-01 | Kansas | Ramsey6 |  | 138 |  | 290 | uprate | L7 | WI | 5.7 |  |  | 100 |  |  | Proposed | 100000 | Eng |  |  | ATC Provisional status | 2005-07-11 | MTEP06 | ATC - Wenchun Zhu | G051 | Y | N | Y |  | Interconnection
863 | 2006-04-05 | BR | C-WUMS | ATC LLC | 877 | 2006-03-16 | new100 | 2009-06-01 | Oak Creek | Ramsey |  | 138 |  | 293 | reconductor (need 382 MVA for A035) | L7 | WI | 8.5 |  |  | 100 |  |  | Proposed | 400000 | Eng |  |  |  | 2005-07-11 | MTEP06 | Wenchun Zhu | G051, A035 | Y | N | Y | ATC zone 5 | Network | Y
864 | 2006-04-05 | BR | C-WUMS | ATC LLC | 877 | 2006-03-16 | new100 | 2009-06-01 | Oak Creek | Allerton |  | 138 |  | 242 | reconductor | L7 | WI | 5.4 |  |  | 100 |  |  | Proposed | 2000000 | Eng |  |  |  | 2005-07-11 | MTEP06 | Wenchun Zhu | G051, A035 | Y | N | Y | ATC zone 5 | Network | Y
865 | 2005-07-11 | BR | C-WUMS | ATC LLC | 877 | 2006-03-16 | new100 | 2009-06-01 | Oak Creek | Relaying replacements |  | 230 |  |  | replace relaying | L7 | WI |  |  |  | 100 |  |  | Proposed | 3000000 | Eng |  |  |  | 2005-07-11 | MTEP06 |  | G051 | Y | N | Y |  | Interconnection
869 | 2006-07-05 | BR | C-WUMS | ATC LLC | 877 | 2006-03-16 | new100 | 2009-06-01 | Harbor | Kansas |  | 138 |  | 157 | loop Ramsey5-Harbor into Norwich and Kansas to form Ramsey-Norwich and Harbor-Kansas | L7 | WI | 2.72 |  |  | 100 |  |  | Proposed | 2000000 | Eng |  |  | ATC Provisional status | 2005-07-11 | MTEP06 | ATC - Wenchun Zhu | G051, A035 | Y | N | Y |  | Interconnection | Y
868 | 2006-07-05 | BR | C-WUMS | ATC LLC | 877 | 2006-03-16 | new100 | 2009-06-01 | Ramsey | Norwich |  | 138 |  | 288 | loop Ramsey5-Harbor into Norwich and Kansas to form Ramsey-Norwich and Harbor-Kansas | L7 | WI | 3 |  |  | 100 |  |  | Proposed | 2100000 | Eng |  |  | ATC Provisional status | 2005-07-11 | MTEP06 | ATC - Wenchun Zhu | G051, A035 | Y | N | Y |  | Interconnection | Y
867 | 2005-07-11 | BR | C-WUMS | ATC LLC | 877 | 2006-03-16 | new100 | 2009-06-01 | Oak Creek | Expand 345 kV switchyard to interconnect new generator |  | 345 |  |  | expand switchyard to interconnect new generator | L7 | WI |  |  |  | 100 |  |  | Proposed | 10800000 | Eng |  |  |  | 2005-07-11 | MTEP06 |  | G051 | Y | N | Y |  | Interconnection
866 | 2005-07-11 | BR | C-WUMS | ATC LLC | 877 | 2006-03-16 | new100 | 2009-06-01 | Pleasant Prairie | replace two circuit breakers |  | 345 |  |  | replace circuit breakers | L7 | WI |  |  |  | 100 |  |  | Proposed | 2100000 | Eng |  |  |  | 2005-07-11 | MTEP06 |  | G051 | Y | N | Y |  | Interconnection
887 | 2006-07-05 | BR | C-WUMS | ATC LLC | 887 | 2005-07-11 | new110 | 2009-06-01 | Bain | New 345 kV bus |  | 345 |  |  | construct 345 kV bus | L7 | WI | [6 empty] | Proposed | 2100000 | Eng |  |  | ATC Provisional status. Further analysis required. | 2005-07-11 | MTEP06 | ATC - Wenchun Zhu |  | Y | N | Y
1985 | 2006-07-05 | LN | C-WUMS | ATC LLC | 1267 | 2006-07-05 | new1 | 2009-06-01 | Verona | Oak Ridge | 1 | 138 |  |  | line to new T-D substation |  | WI | [6 empty] | Proposed |  |  |  |  | Replaces Montrose-Oakridge 138-kV | 2006-07-05 |  | ATC - Wenchun Zhu |  | Y | N | Y
1984 | 2006-07-05 | TX | C-WUMS | ATC LLC | 1267 | 2006-07-05 | new1 | 2009-06-01 | Verona 138/69 | transformer | 1 | 138 | 69 | 100 |  |  | WI | [6 empty] | Proposed |  |  | Replaces Montrose 138-69 kV Tr project |  |  | 2006-07-05 |  | ATC - Wenchun Zhu |  | Y | N | Y
1986 | 2006-07-05 | CAP | C-WUMS | ATC LLC | 1268 | 2006-07-05 | new2 | 2009-06-01 | Artesion | Capacitor bank |  |  |  | 49 | install 2x 24.9 Mvar capacitor banks |  | WI | [6 empty] | Proposed |  |  |  |  | ATC Provisional status | 2006-07-05 |  | ATC - Wenchun Zhu |  | Y | N | Y
1987 | 2006-07-05 | CAP | C-WUMS | ATC LLC | 1268 | 2006-07-05 | new2 | 2009-06-01 | Kilbourn | Capacitor bank |  |  |  | 32.6 | install 2x 16.3 Mvar capacitor banks |  | WI | [6 empty] | Proposed |  |  |  |  | ATC Provisional status | 2006-07-05 |  | ATC - Wenchun Zhu |  | Y | N | Y
607 | 2006-07-05 | BR | C-WUMS | ATC LLC | 177 | 2006-03-16 | 155 | 2009-12-01 | Gardner Park (new Weston) | Central Wisconsin | 1 | 345 |  | 1200 |  | K6 | WI |  | 47 |  | 100 |  |  | Planned | 90200000 | Eng |  |  | Construction Delay |  |  | ATC - Wenchun Zhu | G144 | Y | N | Y |  | Network
480 | 2006-03-16 | BR | C-WUMS | ATC LLC | 345 | 2005-07-11 | newgrp20 | 2009-12-01 | Morgan | Werner West |  | 345 |  | 1328 | new line | K6 | WI |  | 47 | 50 |  |  | 50 | Planned | 113800000 | Eng |  |  | construction delay |  |  | ATC - Paul Hesse | A013, F009 | Y | N | Y |  |  | Y
608 | 2006-03-16 | BR | C-WUMS | ATC LLC | 345 | 2005-07-11 | newgrp20 | 2009-12-01 | Clintonville | Werner West |  | 138 |  | 288 |  | K6 | WI | 14 | 2 | 50 |  |  | 50 | Planned | 0 | Eng |  |  | construction delay |  |  | ATC - Paul Hesse | A013 | Y | N | Y |  |  | Y
1993 | 2006-07-05 | LN | C-WUMS | ATC LLC |  |  | no Proj | 2009-12-31 | Hiawatha | Pine River | 1 | 69 |  | 191 MVA SE | Maintenance rebuild of 69kV at 138kV standards |  | WI | [6 empty] | Proposed |  |  | Delayed need |  |  | 2006-07-05 |  | ATC - Wenchun Zhu |  | Y | N | Y
896 | 2005-07-11 | BR | C-WUMS | ATC LLC | 352 | 2006-03-16 | newgrp4 | 2009-12-31 | Iron Grove | Substation relocation |  | 138 |  |  | Iron River rename/relocation | K5 | MI |  |  | 25 |  | 25 | 50 | Planned | 5900000 | Eng |  |  |  | 2005-07-11 | MTEP06 |  | A215 | Y | N | Y |  |  | Y
1371 | 2006-07-05 | BR | C-WUMS | ATC LLC | 352 | 2006-03-16 | newgrp4 | 2009-12-31 | Iron Grove | Plains | 1 | 138 |  | 400 MVA SE |  | K5 | WI |  |  | 100 |  |  |  | Planned | 2 |  |  |  | Construction schedule limitations |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 2
1964 | 2006-05-08 | BR | C-WUMS | ATC LLC | 1256 | 2006-05-08 | 1256 | 2010-04-01 | Paddock | Rockdale | 2 | 345 |  | 1430 | add a second circuit (new line) between the existing 345 kV substations Paddock and Rockdale. | K7 | WI | 22.7 | 7.6 |  |  |  | 100 | Proposed | 66360500 |  |  |  |  | 2006-05-08 | MTEP06 | Wenchun Zhu | ATC Access Initiative | Y | N | Y
1370 | 2006-07-05 | BR | C-WUMS | ATC LLC | 574 | 2005-07-11 | 574 | 2010-06-01 | Council Creek 161-138 kV | transformer |  | 161 | 138 | 280 |  | J6 | WI |  |  | 100 |  |  |  | Proposed | 2500000 | Eng |  |  | ATC Provisional status |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 1
858 | 2006-07-05 | BR | C-WUMS | ATC LLC | 574 | 2005-07-11 | 574 | 2010-06-01 | Council Creek | Petenwell |  | 138 |  |  | uprate | J6 | WI | 32 |  | 50 |  |  | 50 | Proposed | 200000 | Eng |  |  | ATC Provisional status | 2005-07-11 | MTEP06 | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 1
859 | 2006-07-05 | BR | C-WUMS | ATC LLC | 574 | 2005-07-11 | 574 | 2010-06-01 | Petenwell | Saratoga |  | 138 |  |  | rebuild/reconductor | J6 | WI | 23 |  | 50 |  |  | 50 | Proposed | 14800000 | Eng |  |  | ATC Provisional status | 2005-07-11 | MTEP06 | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 1
1269 | 2006-07-05 | BR | C-WUMS | ATC LLC | 574 | 2005-07-11 | 574 | 2010-06-01 | Monroe County (XEL) | Council Creek (ATC) | 1 | 161 |  | 530 |  | J6 | WI | 20 |  | 100 |  |  |  | Proposed | 16700000 | Eng |  |  | ATC Provisional status |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 1
873 | 2006-04-05 | BR | C-WUMS | ATC LLC | 877 | 2006-03-16 | new100 | 2010-06-01 | Oak Creek | Nicholson |  | 138 |  | 332 | uprate | L7 | WI | 6.8 |  |  | 100 |  |  | Proposed | 1200000 | Eng |  |  |  | 2005-07-11 | MTEP06 | Wenchun Zhu | G051 | Y | N | Y | ATC zone 5 | Interconnection
870 | 2005-07-11 | BR | C-WUMS | ATC LLC | 877 | 2006-03-16 | new100 | 2010-06-01 | Oak Creek | Expand 345 kV switchyard to interconnect second new generator |  | 345 |  |  | expand switchyard to interconnect second new generator | L7 | WI |  |  |  | 100 |  |  | Proposed | 10800000 | Eng |  |  |  | 2005-07-11 | MTEP06 |  | G051 | Y | N | Y |  | Interconnection
482 | 2005-11-28 | BR | C-WUMS | ATC LLC | 877 | 2006-03-16 | new100 | 2010-06-01 | Oak Creek 345/138 #2 | transformer | 2 | 345 | 138 | 500 |  | L7 | WI |  |  | 25 | 75 |  |  | Planned | 6600000 | Eng |  |  | Studies show a need in 2009, one year earlier than originally thought |  |  |  | G051 | Y | N | Y |  | Interconnection
872 | 2006-04-05 | BR | C-WUMS | ATC LLC | 877 | 2006-03-16 | new100 | 2010-06-01 | Oak Creek | Root River |  | 138 |  | 293 | uprate | L7 | WI |  |  |  | 100 |  |  | Proposed | 600000 | Eng |  |  |  | 2005-07-11 | MTEP06 | Wenchun Zhu | G051 | Y | N | Y | ATC zone 5 | Interconnection
884 | 2006-07-05 | DV | C-WUMS | ATC LLC | 884 | 2005-07-11 | new107 | 2010-06-01 | Spring Green | Capacitor bank |  | 69 |  | 32 Mvar | install 2x 16.3 Mvar capacitor banks | K7 | WI |  |  | 100 |  |  |  | Proposed | 1200000 | Eng |  |  | ATC Provisional status | 2005-07-11 | MTEP06 | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 3
897 | 2005-07-11 | BR | C-WUMS | ATC LLC | 356 | 2006-03-16 | newgrp6 | 2011-06-01 | Rockdale | substation expansion |  | 345 |  |  | expand 345 kV substation | K7 | WI |  |  | 100 |  |  |  | Proposed | 1506733 | Eng |  |  |  | 2005-07-11 | MTEP06 |  |  | Y | N | Y
488 | 2006-03-16 | BR | C-WUMS | ATC LLC | 356 | 2006-03-16 | newgrp6 | 2011-06-01 | West Middleton 345/138 | transformer | 1 | 345 | 138 | 500 |  | K7 | WI |  |  | 100 |  |  |  | Proposed | 7888517 | Eng |  |  | delay is possible due to West Campus generation placed in service in 2005 |  |  | ATC - Paul Hesse |  | Y | N | Y
486 | 2005-07-11 | BR | C-WUMS | ATC LLC | 356 | 2006-03-16 | newgrp6 | 2011-06-01 | West Middleton | Rockdale | 1 | 345 |  | 1200 |  | K7 | WI |  | 35 | 50 |  | 50 |  | Proposed | 63249004 | Eng | [7 empty] | Y | N | Y
1988 | 2006-07-05 | TX | C-WUMS | ATC LLC | 1269 | 2006-07-05 | new3 | 2011-06-01 | Arcadian 345-138kV | transformer | 1 | 345 | 138 | 500 | replace Arcadian 345/138kV transformer #3 |  | WI | [6 empty] | Proposed | 3500000 |  |  |  |  | 2006-07-05 |  | ATC - Wenchun Zhu |  | Y | N | Y
1990 | 2006-07-05 | LN | C-WUMS | ATC LLC | 1270 | 2006-07-05 | new4 | 2011-06-01 | Arcadian | Waukesha | 1 | 138 |  | 426 | Increase line clearance |  | WI | 4 | 0 |  |  |  |  | Proposed |  |  |  |  | ATC Provisional status | 2006-07-05 |  | ATC - Wenchun Zhu |  | Y | N | Y
1989 | 2006-07-05 | LN | C-WUMS | ATC LLC | 1270 | 2006-07-05 | new4 | 2011-06-01 | Arcadian | Waukesha | 2 | 138 |  | 426 | Increase line clearance |  | WI | 4 | 0 |  |  |  |  | Proposed |  |  |  |  | ATC Provisional status | 2006-07-05 |  | ATC - Wenchun Zhu |  | Y | N | Y
1991 | 2006-07-05 | LN | C-WUMS | ATC LLC | 1271 | 2006-07-05 | new5 | 2011-06-01 | Oak Creek | Pennsylvania | 1 | 138 |  | 293 | Increase line clearance |  | WI |  | 0 |  |  |  |  | Proposed |  |  |  |  | ATC Provisional status | 2006-07-05 |  | ATC - Wenchun Zhu |  | Y | N | Y
442 | 2006-03-16 | BR | C-WUMS | ATC LLC | 174 | 2005-07-11 |  | 2012-06-01 | Canal | Dunn Road |  | 138 |  | 400 |  | L6 | WI |  | 7.64 | 60 |  | 10 | 30 | Planned | 4200000 | Eng |  |  | cap at Sister Bay allowed ATC to defer this project |  |  | ATC - Paul Hesse |  | Y | N | Y
1249 | 2006-07-05 | BR | C-WUMS | ATC LLC | 568 | 2005-07-11 |  | 2012-06-01 | North Lake Geneva | White River | 1 | 138 |  | 237 | line to new T-D substation | K7 | WI |  | 1.4 | 100 |  |  |  | Proposed | 1250000 |  | Delayed T-D need |  | ATC Provisional status. Project redefined |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 3
1372 | 2006-07-05 | BR | C-WUMS | ATC LLC | 682 | 2006-02-17 |  | 2012-06-01 | Huiskamp | Blount (convert) | 1 | 138 |  | 290 | convert 69 to 138 kV | J7 | WI | 5 |  |  |  |  | 100 | Proposed | 20000000 | Eng |  |  | further analysis required |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 3
462 | 2006-03-16 | BR | C-WUMS | ATC LLC | 102 | 2006-03-16 | 83 | 2014-06-01 | Cornell | Range Line | 2 | 138 |  | 248 |  | K7 | WI | 2.43 |  |  | 25 |  | 75 | Proposed | 6000000 | Eng |  |  | An operating guide will permit deferring the project about 6 years. |  |  | ATC - Paul Hesse | G014, G093, A130 | Y | N | Y |  | Network | Y
2063 | 2006-07-05 | DV | C-WUMS | ATC LLC | 434 | 2005-07-11 |  | 2015-06-01 | Butternut | Capacitor bank |  | 138 |  | 28.8 Mvar |  | K6 | WI | [5 empty] | 100 | Proposed | 1050000 | Eng |  |  | Provisional. Further study has found 2007 is the appropriate in service date. |  |  | ATC - Wenchun Zhu | A130 | Y | N | Y |  |  | Y
1265 | 2006-07-05 | BR | C-WUMS | ATC LLC | 573 | 2006-07-05 |  | 2016-01-01 | North Madison | West Middleton | 1 | 345 |  | 1200 |  | K7 | WI |  | 20 | 100 |  |  |  | Proposed | 46700000 | Eng |  |  | Long-term Proposed |  |  | ATC - Wenchun Zhu |  | Y | N | Y
1251 | 2006-07-05 | BR | C-WUMS | ATC LLC | 569 | 2005-07-11 |  | 2016-06-01 | South Lake Geneva 138-69 kV | transformer | 1 | 138 | 69 |  |  |  | WI |  |  | 100 |  |  |  | Proposed | 1973000 | Planning MISO |  |  | Delayed Need | 2004-09-27 |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 3
1250 | 2006-07-05 | BR | C-WUMS | ATC LLC | 569 | 2005-07-11 |  | 2016-06-01 | South Lake Geneva | White River | 1 | 138 |  | 355 | line to new T-D substation | K7 | WI |  | 3 | 100 |  |  |  | Proposed | 2500000 | Eng | Delayed need |  | ATC Provisional status |  |  | ATC - Wenchun Zhu |  | Y | N | Y | ATC zone 3
1271 | 2006-07-05 | BR | C-WUMS | ATC LLC | 575 | 2006-03-16 |  | 2016-06-01 | Suamico | Sobieski | 1 | 138 |  |  |  | K6 | WI |  |  | 100 |  |  |  | Proposed | 1510893 |  |  |  | ATC Provisional status |  |  | ATC - Wenchun Zhu |  | Y | N | Y
1270 | 2006-07-05 | BR | C-WUMS | ATC LLC | 575 | 2006-03-16 |  | 2016-06-01 | Pulliam (now Bayport) | Suamico | 1 | 138 |  |  |  | K6 | WI |  |  | 100 |  |  |  | Proposed | 3199539 |  | project redefined |  | ATC Provisional status |  |  | ATC - Wenchun Zhu |  | Y | N | Y
1272 | 2006-07-05 | BR | C-WUMS | ATC LLC | 575 | 2006-03-16 |  | 2016-06-01 | Sobieski | Pioneer | 1 | 138 |  |  |  | K6 | WI |  |  | 100 |  |  |  | Proposed | 1510893 |  |  |  | ATC Provisional status |  |  | ATC - Wenchun Zhu |  | Y | N | Y
103 | 2006-07-05 | BR | C-WUMS | ATC LLC | 89 | 2006-07-05 | 67 | 2018-06-01 | Mill Road (renamed, was Lannon Junction) | transformer |  | 345 | 138 | 500 | transformer | K7 | WI |  |  | 60 |  |  | 40 | Proposed | 29200000 | Eng |  |  | Provisional. Unable to justify due to reduced load projections and Day 2 generation |  |  | ATC - Wenchun Zhu |  | Y | N | Y
893 | 2006-07-05 | BR | C-WUMS | ATC LLC | 341 | 2006-03-16 | newgrp19 | 2018-06-01 | Concord | Bark River |  | 345 |  | 815 | new line | K7 | WI |  | 19 |  |  |  | 100 | Proposed | 50300000 | Eng |  |  | ATC Provisional status |  |  | ATC - Wenchun Zhu |  | Y | N | Y
894 | 2006-07-05 | BR | C-WUMS | ATC LLC | 341 | 2006-03-16 | newgrp19 | 2018-06-01 | Bark River | transformer |  | 345 | 138 | 500 | transformer | K7 | WI | [5 empty] | 100 | Proposed | 8400000 | Eng |  |  | ATC Provisional status |  |  | ATC - Wenchun Zhu |  | Y | N | Y
483 | 2006-07-05 | BR | C-WUMS | ATC LLC | 341 | 2006-03-16 | newgrp19 | 2018-06-01 | Rockdale | Concord (rebuild to dbl ckt 138/345) | 1 | 345 |  | 1200 | rebuild to dbl ckt 138/345 | K7 | WI | 22.6 |  |  |  |  | 100 | Proposed | 22200000 | Eng |  |  | Provisional. Through the use strategic generation dispatch, this project can be deferred until 2018 |  |  | ATC - Wenchun Zhu |  | Y | N | Y
477 | 2006-07-05 | BR | C-WUMS | ATC LLC | 341 | 2006-03-16 | newgrp19 | 2018-06-01 | Concord 345/138 kV | transformer |  | 345 | 138 | 500 |  | K7 | WI | [5 empty] | 100 | Proposed | 12900000 | Eng |  |  | Provisional. Through the use strategic generation dispatch, this project can be deferred until 2018 |  |  | ATC - Wenchun Zhu |  | Y | N | Y
895 | 2006-07-05 | BR | C-WUMS | ATC LLC | 341 | 2006-03-16 | newgrp19 | 2018-06-01 | Bark River | Mill Road |  | 345 |  | 815 | convert 138 to 345 kV | K7 | WI | 11 |  |  |  |  | 100 | Proposed | 800000 | Eng |  |  | ATC Provisional status |  |  | ATC - Wenchun Zhu |  | Y | N | Y
1862 | 2005-12-05 | BR | West | ATC LLC |  |  |  |  | Mullet River 138-69 kV | Transformer |  | 138 | 69 |  | Replacement of Tranformer |  | WI |  |  |  |  | 100 |  | Planned |  |  |  |  | Submitted by MISO |  |  |  | A120 | Y | N | Y |  |  | Y
1861 | 2005-12-05 | BR | West | ATC LLC |  |  |  |  | Atlantic 138-69 kV | Transformer |  | 138 | 69 | 60 | New Transformer |  | WI |  |  |  |  | 100 |  | Planned |  |  |  |  | Submitted by MISO |  |  |  | A105, F006 | Y | N | Y |  |  | Y
1857 | 2005-12-05 | BR | West | ATC LLC |  |  |  |  | Weston | Arpin |  | 345 |  |  | New line |  | WI |  |  |  |  | 100 |  | Planned |  |  |  |  | Submitted by MISO |  |  |  | F009 | Y | N | Y |  |  | Y
3055 | 2006-07-05 | DV | E-MIO | CIN | 823 | 2005-07-11 | X02C8266 | 2006-07-15 | Terminal | Capacitor |  | 69 |  | 28.8 MVAR | Add capacitor | N10 | OH |  |  | 100 |  |  |  | Under Construction | 433433 | Engr |  | Y | Construction Delay |  |  | Jim Doell |  | Y | N | Y
822 | 2005-11-28 | BR | E-MIO | CIN | 842 | 2005-07-11 |  | 2006-11-30 | Blackwell | LGEE Tap |  | 138 |  |  | 138 line for Blackwell 138/69, LGEE circuit | N10 | KY |  |  | 100 |  |  |  | Planned | 589000 | Planning MISO |  | Y |  |  | MTEP06 |  |  | Y | N | Y
821 | 2005-11-28 | BR | E-MIO | CIN | 842 | 2005-07-11 | 302D7779 | 2006-11-30 | Blackwell | transformer |  | 138 | 69 | 150 | 138/69 | N10 | KY |  |  | 100 |  |  |  | Planned | 1977000 | Planning MISO |  | Y |  |  | MTEP06 |  |  | Y | N | Y
3058 | 2005-07-11 | DV | E-MIO | CIN | 765 | 2005-07-11 |  | 2006-12-01 | Cloverdale | Capacitor |  | 138 |  | 43.2 Mvar | Add capacitor | L10 | IN |  |  | 100 |  |  |  | Planned | 524860 | Engr |  | Y | [5 empty] | Y | N | Y
3059 | 2005-07-11 | DV | E-MIO | CIN | 825 | 2005-07-11 | T | 2006-12-01 | Wabash | Capacitor |  | 69 |  | 28.8 MVAR | Add capacitor | M9 | IN |  |  | 100 |  |  |  | Planned | 459500 | Engr |  | Y | [5 empty] | Y | N | Y
815 | 2005-07-11 | DV | E-MIO | CIN | 836 | 2005-07-11 | AE | 2006-12-01 | Inland Container | Capacitor |  | 69 |  | 21.6 MVAR | Add capacitor | L9 | IN |  |  | 100 |  |  |  | Planned | 500000 | Plan |  | Y |  |  | MTEP06 |  |  | Y | N | Y
1848 | 2005-11-28 | BR | E-MIO | CIN | 1197 | 2005-11-28 | X03C7992 | 2006-12-01 | Evendale |  |  | 138 | 34.5 |  | Replace failed transformer as two winding. New transf. To be connected to 138kV bus 2. |  | OH |  |  | 100 |  |  |  | Planned | [5 empty] | 2005-11-28 | MTEP06 |  |  | Y | N | Y
1292 | 2006-03-27 | BR | E-MIO | CIN | 619 | 2006-03-10 |  | 2006-12-31 | IPL Petersburg | 345kV breaker |  | 345 |  |  | Complete breaker and half scheme at Petersburg Plant. IPL total estimate 1,100,000. 200k is Cinergy share of project. | M10 | IN | 0 | 0 | 100 |  |  |  | Planned | 200000 | Plan |  | Y |  |  |  | Jim Doell |  | Y | N | Y
1308 | 2006-03-27 | BR | E-MIO | CIN | 631 | 2005-07-11 |  | 2006-12-31 | Columbus | Seymour | 1 | 138 |  | 179 | replace 600A switches at Columbus, limit becomes 397ACSR30X7 at 179MVA. | M10 | IN | 0 | 0 | 100 |  |  |  | Planned | 65695 | Engr |  | Y |  |  |  | Jim Doell |  | Y | N | Y
3048 | 2005-11-28 | DV | E-MIO | CIN | 819 | 2005-07-11 | N | 2006-12-31 | Bedford | Capacitor |  | 69 |  | 50.4 MVAR | Add capacitor | M10 | IN |  |  | 100 |  |  |  | Planned | 731664 | Engr |  | Y | [5 empty] | Y | N | Y
3050 | 2005-07-11 | DV | E-MIO | CIN | 820 | 2005-07-11 | O | 2006-12-31 | Loogootee | Capacitor |  | 69 |  | 7.2 MVAR | Add capacitor | L10 | IN |  |  | 100 |  |  |  | Planned | 474134 | Engr |  | Y | [5 empty] | Y | N | Y
3051 | 2005-07-11 | DV | E-MIO | CIN | 821 | 2005-07-11 | P | 2006-12-31 | Orleans South | Capacitor |  | 69 |  | 14.4 MVAR | Add capacitor | M10 | IN |  |  | 100 |  |  |  | Planned | 585618 | Engr |  | Y | [5 empty] | Y | N | Y
3057 | 2006-03-27 | DV | E-MIO | CIN | 824 | 2005-07-11 | S | 2006-12-31 | Wilder 2 | Capacitor |  | 69 |  | 28.8 MVAR | Add capacitor | N10 | KY |  |  | 100 |  |  |  | Planned | 445485 | Engr |  | Y |  |  |  | Jim Doell |  | Y | N | Y
816 | 2005-07-11 | DV | E-MIO | CIN | 837 | 2005-07-11 | AF | 2006-12-31 | New Albany | Capacitor |  | 69 |  | 28.8 MVAR | Add capacitor | M10 | IN |  |  | 100 |  |  |  | Planned | 500000 | Plan |  | Y |  |  | MTEP06 |  |  | Y | N | Y
817 | 2005-07-11 | DV | E-MIO | CIN | 838 | 2005-07-11 | AG | 2006-12-31 | Speed | Capacitor |  | 138 |  | 57.6 MVAR | Add capacitor | M10 | IN |  |  | 100 |  |  |  | Planned | 500000 | Plan |  | Y |  |  | MTEP06 |  |  | Y | N | Y
1847 | 2006-07-05 | BR | E-MIO | CIN | 1196 | 2005-11-28 | 602C5687 | 2006-12-31 | Kokomo Highland Park | New London | 1 | 230 |  | 405 | Replace Kokomo Highland Park 23009 800A wave trap with a 1200A wave trap. |  | IN |  |  | 100 |  |  |  | Planned | [5 empty] | 2005-11-28 | MTEP06 | Jim Doell |  | Y | N | Y
1846 | 2006-07-05 | BR | E-MIO | CIN | 1196 | 2005-11-28 | 602F6290 | 2006-12-31 | New London | Kokomo Highland Park | 1 | 230 |  | 405 | Replace New London 23009 800A wave trap with a 1200A wave trap. |  | IN |  |  | 100 |  |  |  | Planned | 29671.83 | Engr |  |  |  | 2005-11-28 | MTEP06 | Jim Doell |  | Y | N | Y
1854 | 2006-07-05 | BR | E-MIO | CIN | 1201 | 2005-11-28 | 804C5822 | 2006-12-31 | Oakland City | Princeton | 1 | 138 |  | 287 | Uprate line to 100C operating temperature by adding 3 structures. |  | IN |  |  | 100 |  |  |  | Planned | 111331 | Engr |  |  | Due to storm restoration work on the 345 lines in southern Indiana, outages cannot be taken on the 13863/34516 lines until early Fall. | 2005-11-28 | MTEP06 | Jim Doell |  | Y | N | Y
1949 | 2006-03-27 | BR | E-MIO | CIN | 1251 | 2006-03-27 | 602C5687 | 2006-12-31 | Kokomo Highland Park 23008 Wave Trap | Carmel 146th St Jct |  | 230 |  | 405 | Replace 800A wave trap with a 2000A wave trap. Increase 230kV line rating to Carmel 146th St Jct. |  | IN |  |  | 100 |  |  |  | Planned | 30000 | Plan |  | Y | [5 empty] | Y | N | Y
1951 | 2006-03-27 | BR | E-MIO | CIN | 1252 | 2006-03-27 | 602C5687 | 2006-12-31 | Kokomo Highland Park 23028 Wave Trap | Thorntown |  | 230 |  | 405 | Replace 800A wave trap with a 2000A wave trap. Increase 230kV line rating to Thorntown. |  | IN |  |  | 100 |  |  |  | Planned | 30000 | Plan | 8187391.83 | Y | [5 empty] | Y | N | Y
1845 | 2006-07-05 | BR | E-MIO | CIN | 1195 | 2005-11-28 | 604E6256 | 2007-05-01 | Cloverdale | Cloverdale Ethanol | 1 | 138 |  |  | Construct new 138kV line from Cloverdale to new Putnam Energy ethanol plant. |  | IN |  |  | 100 |  |  |  | Planned | 229811 | Engr |  |  | In service date tied to customer construction schedule. | 2005-11-28 | MTEP06 | Jim Doell |  | Y | N | Y
182 | 2005-07-11 | BR | E-MIO | CIN | 42 | 2005-07-11 | 17 | 2007-06-01 | Bedford | Shawswick | 1 | 138 |  | 306 | Reconductor Bedford to Shawswick section of 13829 line. | M10 | IN | 7.1 |  | 100 |  |  |  | Planned | 2110106 | Engr |  | Y | [5 empty] | Y | N | Y
366 | 2005-07-11 | BR | E-MIO | CIN | 115 | 2005-07-11 | 86 | 2007-06-01 | New London | Webster | 1 | 230 |  | 800 | reconductor | M9 | IN | 12 |  | 100 |  |  |  | Planned | 9455194 | Engr |  | Y | [5 empty] | Y | N | Y
367 | 2005-07-11 | BR | E-MIO | CIN | 116 | 2005-07-11 | 87 | 2007-06-01 | Westwood | Dequine | 1 | 345 |  | 1200 | Add 2nd 345kV line | L9 | IN |  | 2 | 100 |  |  |  | Planned | 588366 | Engr |  | Y | [5 empty] | Y | N | Y
357 | 2005-07-11 | BR | E-MIO | CIN | 116 | 2005-07-11 | 87 | 2007-06-01 | Westwood 345/138 | transformer | 2 | 345 | 138 | 336 | Add 2nd 345/138 transformer | L9 | IN |  |  | 100 |  |  |  | Planned | 6093584 | Engr |  | Y | [5 empty] | Y | N | Y
1307 | 2005-07-11 | BR | E-MIO | CIN | 116 | 2005-07-11 |  | 2007-06-01 | West Lafayette | Cumberland | 1 | 138 |  | 179 | replace 600A switches | M9 | IN | 0 | 0 | 100 |  |  |  | Planned | 154757 | Engr |  | Y | [5 empty] | Y | N | Y
356 | 2005-07-11 | BR | E-MIO | CIN | 199 | 2005-07-11 |  | 2007-06-01 | Kokomo 230/138 | transformer | 2 | 230 | 138 | 200 | Add fourth 230/138kV transformer. | M9 | IN |  |  | 100 |  |  |  | Planned | 3278756 | Engr |  | Y | [5 empty] | Y | N | Y
618 | 2005-07-11 | BR | E-MIO | CIN | 200 | 2005-07-11 |  | 2007-06-01 | West Lafayette Purdue | Purdue NW Tap | 1 | 138 |  | 179 | Upgrade switches at West Lafayette Purdue. | L9 | IN | 7.2 |  | 100 |  |  |  | Planned | 9877 | Engr |  | Y | [5 empty] | Y | N | Y
1300 | 2006-07-05 | BR | E-MIO | CIN | 624 | 2005-07-11 |  | 2007-06-01 | Cloverdale | Plainfield South | 1 | 138 |  | No change | Upgrade static and grounding | L10 | IN | 24.3 | 0 | 100 |  |  |  | Planned | 2387209 | Engr |  | Y | his was a project to increase the reliability for this line. Project changed from reconductor to upgrading static and grounding only. |  |  | Jim Doell |  | Y | N | Y
1853 | 2005-11-28 | DV | E-MIO | CIN | 627 | 2005-07-13 |  | 2007-06-01 | Buffington Reactor |  |  | 138 |  |  | Remove reactor when Kenton to West End project is completed. |  | KY |  |  | 100 |  |  |  | Planned | [5 empty] | 2005-11-28 | MTEP06 |  |  | Y | N | Y
1953 | 2006-03-27 | BR | E-MIO | CIN | 627 | 2005-07-13 | 304D7834 | 2007-06-01 | Crescent | West End |  | 138 |  | 239 | 3 wires of existing 6 wire circuit will be used for the new Kenton to West End circuit, lowering the rating of Crescent to West End. |  |  |  |  | 100 |  |  |  | Planned |  |  |  | Y | [5 empty] | Y | N | Y
1305 | 2005-07-11 | BR | E-MIO | CIN | 628 | 2005-07-11 |  | 2007-06-01 | Kokomo Highland Park | Kokomo Chrysler | 1 | 138 |  | 179 | Kok 13879 Uprate conductor to 100C operating temp | M9 | IN | 3 | 0 | 100 |  |  |  | Planned | 100000 | Plan |  | Y | [5 empty] | Y | N | Y
1306 | 2005-07-11 | BR | E-MIO | CIN | 629 | 2005-07-11 | 628A | 2007-06-01 | Kokomo Highland Park | Kokomo Delco | 1 | 138 |  | 179 | Kok 13887 Uprate conductor to 100C operating temp | M9 | IN | 3.78 | 0 | 100 |  |  |  | Planned | 100000 | Plan |  | Y | [5 empty] | Y | N | Y
3060 | 2005-07-11 | DV | E-MIO | CIN | 766 | 2005-07-11 |  | 2007-06-01 | Clarksville | Capacitor |  | 138 |  | 57.6 Mvar | Add capacitor | M10 | IN |  |  | 100 |  |  |  | Planned | 738662 | Engr |  | Y | [5 empty] | Y | N | Y
3062 | 2005-07-11 | DV | E-MIO | CIN | 767 | 2005-07-11 |  | 2007-06-01 | Greenfield Hastings Park | Capacitor |  | 138 |  | 57.6 Mvar | Add capacitor | M9 | IN |  |  | 100 |  |  |  | Planned | 598722 | Engr |  | Y | [5 empty] | Y | N | Y
3049 | 2005-11-28 | DV | E-MIO | CIN | 795 | 2005-07-11 |  | 2007-06-01 | Geist | Capacitor |  | 69 |  | 36 MVAR | Add capacitor | M9 | IN |  |  | 100 |  |  |  | Planned | 452788 | Engr |  | Y | [5 empty] | Y | N | Y
809 | 2005-07-11 | BR | E-MIO | CIN | 806 | 2005-07-11 | A | 2007-06-01 | Gwynneville | Gwynneville 69108 Jct | 1 | 69 |  | 153 | New 69kV line from Gwynneville to a new Jct between Arlington Jct and Morristown. Deenergize section from 108 Jct to 166 Jct. Gwynneville-Jct-Arlington Jct | M10 | IN |  | 4.1 | 100 |  |  |  | Planned | 1474521 | Engr |  | Y |  |  | MTEP06 |  |  | Y | N | Y
810 | 2005-07-11 | BR | E-MIO | CIN | 806 | 2005-07-11 | A | 2007-06-01 | Gwynneville | Gwynneville 69140 Jct | 1 | 69 |  | 153 | New 69kV line from Gwynneville to a new Jct between Arlington Jct and Carthage | M10 | IN |  | 6.3 | 100 |  |  |  | Planned | 3953352 | Engr |  | Y |  |  | MTEP06 |  |  | Y | N | Y
808 | 2005-07-11 | BR | E-MIO | CIN | 806 | 2005-07-11 | A | 2007-06-01 | Gwynneville | transformer | 1 | 345 | 69 | 150 | Add 150 MVA 345/69 kV xfr | M10 | IN |  |  | 100 |  |  |  | Planned | 5175365 | Engr |  | Y |  |  | MTEP06 |  |  | Y | N | Y
811 | 2005-07-11 | BR | E-MIO | CIN | 806 | 2005-07-11 | A | 2007-06-01 | Gwynneville | Gwynneville 69166 Jct | 1 | 69 |  | 153 | New 69kV line from Gwynneville to a new Jct between Arlington Jct and Morristown. Reconductor from Jct to Morristown. Gwynneville-Jct-Morristown. | M10 | IN | 2 | 3.3 | 100 |  |  |  | Planned | 1173812 | Engr |  | Y |  |  | MTEP06 |  |  | Y | N | Y
1302 | 2006-03-27 | BR | E-MIO | CIN | 810 | 2005-07-11 | 804G6582 | 2007-06-01 | Bloomington | transformer | 3 | 230 | 69 | 200 | Add 230/69kV Bk3 | M10 | IN | 0 | 0 | 100 |  |  |  | Planned | 3986059 | Engr |  | Y |  |  |  | Jim Doell |  | Y | N | Y
814 | 2005-07-11 | DV | E-MIO | CIN | 811 | 2005-07-11 | F | 2007-06-01 | Evendale 2 | Capacitor |  | 69 |  | 21.6 MVAR | Add capacitor | N10 | OH |  |  | 100 |  |  |  | Planned | 390805 | Engr |  | Y |  |  | MTEP06 |  |  | Y | N | Y
3061 | 2005-07-11 | DV | E-MIO | CIN | 811 | 2005-07-11 | F | 2007-06-01 | Evendale 1 | Capacitor |  | 69 |  | 21.6 MVAR | Add capacitor | N10 | OH |  |  | 100 |  |  |  | Planned | 390805 | Engr |  | Y | [5 empty] | Y | N | Y
3063 | 2005-07-11 | DV | E-MIO | CIN | 826 | 2005-07-11 | U | 2007-06-01 | Kokomo Webster St | Capacitor |  | 69 |  | 28.8 MVAR | Add capacitor | M9 | IN |  |  | 100 |  |  |  | Planned | 467860 | Engr |  | Y | [5 empty] | Y | N | Y
3065 | 2005-07-11 | DV | E-MIO | CIN | 828 | 2005-07-11 | W | 2007-06-01 | Northgreen | Capacitor |  | 69 |  | 14.4 MVAR | Add capacitor | N10 | OH |  |  | 100 |  |  |  | Planned | 406671 | Engr |  | Y | [5 empty] | Y | N | Y
3067 | 2005-07-11 | DV | E-MIO | CIN | 830 | 2005-07-11 | Y | 2007-06-01 | Thorntown | Capacitor |  | 69 |  | 28.8 MVAR | Add capacitor | M9 | IN |  |  | 100 |  |  |  | Planned | 456723 | Engr |  | Y | [5 empty] | Y | N | Y
818 | 2006-03-27 | DV | E-MIO | CIN | 839 | 2005-07-11 | AH | 2007-06-01 | Crawfordsville | Capacitor |  | 138 |  | 28.8 MVAR | Add capacitor | L9 | IN |  |  | 100 |  |  |  | Planned | 500000 | Plan |  | Y |  |  | MTEP06 | Jim Doell |  | Y | N | Y
823 | 2005-07-11 | BR | E-MIO | CIN | 849 | 2005-07-11 | AR | 2007-06-01 | Peabody Jct | Jasonville | 1 | 138 |  | 246 | Replace Peabody Jct 600A switches with 1200A towards Jasonville in the 13821 line, 804F6402 | L10 | IN |  |  | 100 |  |  |  | Planned | 159170.5 | Engr |  | Y |  |  | MTEP06 |  |  | Y | N | Y
824 | 2005-07-11 | BR | E-MIO | CIN | 849 | 2005-07-11 | AR | 2007-06-01 | Peabody Jct | Farmersburg Jct | 1 | 138 |  | 246 | Replace Peabody Jct 600A switches with 1200A towards Farmersburg Jct in the 13821 line, 804F6402 | L10 | IN |  |  | 100 |  |  |  | Planned | 159170.5 | Engr |  | Y |  |  | MTEP06 |  |  | Y | N | Y
1849 | 2005-11-28 | DV | E-MIO | CIN | 1198 | 2005-11-28 | 802F6503 | 2007-06-01 | Bedford |  |  | 345 |  |  | Add motors and automation to the 34506 and 34521 line switches. |  | IN |  |  | 100 |  |  |  | Planned | 152390.14 | Engr |  |  |  | 2005-11-28 | MTEP06 |  |  | Y | N | Y
1943 | 2006-03-27 | BR | E-MIO | CIN | 1242 | 2006-03-27 | 604F6524 | 2007-06-01 | Linden Ethanol |  |  | 138 | 12 |  | Install 1200A switch in 13819 line for new Ethanol plant between Crawfordsville and Tipmont Concord Jct |  | IN |  |  | 100 |  |  |  | Planned | 173830 | Engr |  | Y | [5 empty] | Y | N | Y
1944 | 2006-03-27 | BR | E-MIO | CIN | 1243 | 2006-03-27 | 104E7901 | 2007-06-01 | Port Union | Allen |  | 69 |  | 153 | Construct new 69kV line from Port Union to Allen. |  | OH |  |  | 100 |  |  |  | Planned | 808811 | Engr |  | Y | [5 empty] | Y | N | Y
1956 | 2006-07-05 | DV | E-MIO | CIN | 1248 | 2006-03-27 | X02C8677 | 2007-06-01 | Miami Fort GT |  |  | 69 |  | 21.6MVAR | Install 21.6MVAR cap bk. |  | OH |  |  | 100 |  |  |  | Planned | 551247 | Engr |  | Y |  |  |  | Jim Doell |  | Y | N | Y
1954 | 2006-07-05 | DV | E-MIO | CIN | 1250 | 2006-03-27 | X02C8675 | 2007-06-01 | Kings Mills | Capacitor |  | 69 |  | 28.8MVAR | Install 28.8 MVAR 69kV capacitor. |  | OH |  |  | 100 |  |  |  | Planned | 461564 | Engr |  | Y |  |  |  | Jim Doell |  | Y | N | Y
1978 | 2006-07-05 | BR | E-MIO | CIN | 1262 | 2006-07-05 | 702G6641 | 2007-06-01 | HE Durgee Rd |  |  | 138 |  |  | HE 138/12 kV substation. |  | IN |  |  | 100 |  |  |  | Planned | 227341 | Engr |  | Y |  | 2006-07-05 |  | Jim Doell |  | Y | N | Y
3068 | 2005-07-11 | DV | E-MIO | CIN | 831 | 2005-07-11 | Z | 2007-06-30 | Greensburg | Capacitor |  | 69 |  | 28.8 MVAR | Add capacitor | M10 | IN |  |  | 100 |  |  |  | Planned | 481738 | Engr |  | Y | [5 empty] | Y | N | Y
1301 | 2006-07-05 | BR | E-MIO | CIN | 625 | 2006-07-05 |  | 2007-12-01 | Pierce/Beckjord 345/138 kV | transformer | C | 345 | 138 | 172 | Add third 345/138kV xfr 400 MVA connected to Beckjord 138kV North Bus. | N10 | OH |  |  | 100 |  |  |  | Proposed | 1600000 | Plan |  | N | In service date changed to allow further study and refinement of the scope of work. |  |  | Jim Doell |  | Y | N | Y
1288 | 2006-07-05 | BR | E-MIO | CIN | 847 | 2005-07-11 | AP | 2007-12-31 | Gallagher RAT 11 | transformer | 11 | 138 | 4 |  | Install 138/4kV RAT 11and relocate the 138kV transfer breaker at Gallagher Gen Sta. | M10 | IN | 0 | 0 |  | 100 |  |  | Planned | 412561 | Engr | 49861628.14 | Y | In service date tied to generation construction schedule. |  |  | Jim Doell |  | Y | N | Y
358 | 2005-11-28 | BR | E-MIO | CIN | 91 | 2005-07-11 | 72 | 2008-06-01 | Hillcrest 345/138 | transformer | 1 | 345 | 138 | 450 | Add new 345/138 substation | N10 | OH |  |  | 100 |  |  |  | Planned | 5693185.59 | Engr |  | Y | [5 empty] | Y | N | Y
362 | 2005-07-11 | BR | E-MIO | CIN | 91 | 2005-07-11 | 72 | 2008-06-01 | Hillcrest | Eastwood | 1 | 138 |  | 304 | Add new line | N10 | OH |  | 8 | 100 |  |  |  | Planned | 4613151 | Engr |  | Y | [5 empty] | Y | N | Y
536 | 2005-07-11 | BR | E-MIO | CIN | 201 | 2005-07-11 |  | 2008-06-01 | NW Tap | West Lafayette | 1 | 138 |  | 240 | Changing out switches to achieve conductor rating. | L9 | IN | 0 |  | 100 |  |  |  | Planned | 100000 | Plan |  | Y | [5 empty] | Y | N | Y
3069 | 2005-07-11 | DV | E-MIO | CIN | 832 | 2005-07-11 | AA | 2008-06-01 | Lebanon | Capacitor |  | 69 |  | 21.6 MVAR | Add capacitor | M9 | IN |  |  | 100 |  |  |  | Planned | 411481 | Engr |  | Y | [5 empty] | Y | N | Y
1960 | 2006-03-27 | BR | E-MIO | CIN | 1255 | 2006-03-27 | 302G8835 | 2008-06-01 | Covington |  |  | 138 | 13 |  | Construct 138/12 kV substation |  | KY |  |  | 100 |  |  |  | Planned |  |  |  | Y | [5 empty] | Y | N | Y
1976 | 2006-07-05 | BR | E-MIO | CIN | 1260 | 2006-07-05 | 103G8856 | 2008-06-01 | Obannonville |  |  | 138 | 34 |  | 60MVA 138/34kV substation loop 5489 into sub. |  |  |  |  | 100 |  |  |  | Planned | 2006475 | Engr |  | Y |  | 2006-07-05 |  | Jim Doell |  | Y | N | Y
1977 | 2006-07-05 | BR | E-MIO | CIN | 1261 | 2006-07-05 | 603B5453 | 2008-06-01 | Lafayette Shadeland |  |  | 138 | 12 |  | 22 MVA sub |  | IN |  |  | 100 |  |  |  | Planned | 1306341 | Engr |  | Y |  | 2006-07-05 |  | Jim Doell |  | Y | N | Y
825 | 2005-07-11 | BR | E-MIO | CIN | 850 | 2005-07-11 | AS | 2008-12-31 | Northside | CMC | 1 | 138 |  | 306 | New 138kV line 704F6376 | M10 | IN |  | 4 | 100 |  |  |  | Planned | 3263000 | Planning MISO |  | Y |  |  | MTEP06 |  |  | Y | N | Y
1955 | 2006-03-27 | BR | E-MIO | CIN | 1254 | 2006-03-27 | 704G6587 | 2008-12-31 | Charlestown | CMC |  | 138 |  | 306 | Construct 8.5 mi. of 138kV line from Charlestown to CMC. |  | IN |  |  | 100 |  |  |  | Planned |  |  | 17393633.59 | Y | [5 empty] | Y | N | Y
184 | 2005-07-11 | BR | E-MIO | CIN | 42 | 2005-07-11 | 17 | 2009-06-01 | Shawswick | Pleasant Grove | 1 | 138 |  | 306 | Reconductor | M10 | IN | 18.3 |  | 100 |  |  |  | Planned | 4719516 | Engr |  | Y | [5 empty] | Y | N | Y
181 | 2005-07-11 | BR | E-MIO | CIN | 42 | 2005-07-11 | 17 | 2009-06-01 | Airport Road Jct | Seymour | 1 | 138 |  | 306 MVA | Reconductor | M10 | IN | 2.2 | 0 | 100 | 0 | 0 | 0 | Planned | 752906 | Engr |  | Y | Pleasant Grove to Airport Rd Jct to Seymour is one Cinergy budget project. | 2003-06-03 | MTEP03 |  |  | Y | N | Y
183 | 2005-07-11 | BR | E-MIO | CIN | 42 | 2005-07-11 | 17 | 2009-06-01 | Pleasant Grove | Airport Road Jct | 1 | 138 |  | 306 | Reconductor | M10 | IN | 9.3 |  | 100 |  |  |  | Planned | 3388077 | Engr |  | Y | Pleasant Grove to Ariport Rd Jct to Seymour is one budget project. |  |  |  |  | Y | N | Y
1304 | 2006-07-05 | BR | E-MIO | CIN | 627 | 2005-07-13 | 304D7834 | 2009-06-01 | Kenton | West End | 1 | 138 |  | 239 | Add new line | N10 | KY-OH | 4.5 | 4.3 | 100 |  |  |  | Planned | 1980041 | Engr |  | Y | The addition of the 3rd 345/138 kV transformer at Pierce/Beckjord delays the need for this project. |  |  | Jim Doell |  | Y | N | Y
1309 | 2005-07-11 | BR | E-MIO | CIN | 632 | 2005-07-11 |  | 2009-06-01 | Gallagher | HE Georgetown | 1 | 138 |  | 202 | reconducgtor 250CU, 477ACSR already 100C (no cost) | M10 | IN | 2.8 | 0 | 100 |  |  |  | Planned | 1065110 | Engr |  | Y | [5 empty] | Y | N | Y
812 | 2005-07-11 | BR | E-MIO | CIN | 807 | 2005-07-11 | B | 2009-06-01 | Dresser 345/138 Bk1 | transformer | 1 | 345 | 138 | 523 | Upgrade limiting equipment to achieve full transformer rating | L10 | IN |  |  | 100 |  |  |  | Planned | 429000 | Planning MISO |  | Y |  |  | MTEP06 |  |  | Y | N | Y
813 | 2005-07-11 | BR | E-MIO | CIN | 807 | 2005-07-11 | B | 2009-06-01 | Dresser 345/138 Bk2 | transformer | 2 | 345 | 138 | 543 | Upgrade limiting equipment to achieve full transformer rating | L10 | IN |  |  | 100 |  |  |  | Planned | 429000 | Planning MISO |  | Y |  |  | MTEP06 |  |  | Y | N | Y
3070 | 2005-11-28 | DV | E-MIO | CIN | 833 | 2005-07-11 | AB | 2009-06-01 | Rochester 2 | Capacitor |  | 69 |  | 21.6 MVAR | Add capacitor | M9 | IN |  |  | 100 |  |  |  | Planned | 500000 | Plan |  | Y | [5 empty] | Y | N | Y
1310 | 2005-07-11 | BR | E-MIO | CIN | 844 | 2005-07-13 | AM | 2009-06-01 | Newtown | transformer | 1 | 138 | 69 |  | Add new 138/69kV substation | N10 | OH | 0 | 0 | 100 |  |  |  | Planned | 4198021 | Engr |  | Y | [5 empty] | Y | N | Y
1983 | 2006-07-05 | DV | E-MIO | CIN | 1266 | 2006-07-05 | 502G6689 | 2009-06-01 | Hortonville | Capacitor |  | 69 |  | 36 MVAR | Install 69kV 36MVAR cap bank at Hortonville |  | IN |  |  | 100 |  |  |  | Planned | 500000 | Plan |  | Y |  | 2006-07-05 |  | Jim Doell |  | Y | N | Y
1290 | 2006-07-05 | BR | E-MIO | CIN | 618 | 2005-07-11 | X02C7985 | 2009-12-31 | Beckjord | (rebuild substation) |  | 138 |  |  | rebuild substation so it can be tied together under normal conditions | N10 | OH | 0 | 0 | 100 |  |  |  | Proposed | 1738266 | Engr |  | N | Change in service date to allow time to fully develop plan for this project. |  |  | Jim Doell |  | Y | N | Y
1979 | 2006-07-05 | BR | E-MIO | CIN | 852 | 2006-07-05 | 604F6348 | 2009-12-31 | Crawfordsville | Tipmont Concord Jct |  | 138 |  | 306 | 13819 reconductor with 954ACSR 100C | L9 | IN | 17.4 |  | 100 |  |  |  | Planned | 6142189 | Engr |  | Y |  | 2006-07-05 |  | Jim Doell |  | Y | N | Y
827 | 2006-03-27 | BR | E-MIO | CIN | 852 | 2005-07-11 | 604F6351 | 2009-12-31 | Lafayette Southeast | Tipmont Concord Jct | 1 | 138 |  | 306 | 13819 reconductor with 954ACSR 100C 604F6351 | L9 | IN | 8 |  | 100 |  |  |  | Planned | 2425000 | Planning MISO | 28267126 | Y |  |  | MTEP06 | Jim Doell |  | Y | N | Y
3072 | 2005-07-11 | DV | E-MIO | CIN | 835 | 2005-07-11 | AD | 2010-06-01 | Pittsboro | Capacitor |  | 69 |  | 14.4 MVAR | Add capacitor | M9 | IN |  |  | 100 |  |  |  | Planned | 500000 | Plan |  | Y | [5 empty] | Y | N | Y
1843 | 2005-11-28 | BR | E-MIO | CIN | 1193 | 2005-11-28 | 104F8436 | 2010-06-01 | Nickel |  |  | 138 |  |  | Extend 5680 through new Nickel 138/12 sub to be built on development property |  | OH |  |  | 100 |  |  |  | Planned | 150376.81 | Engr |  |  |  | 2005-11-28 | MTEP06 |  |  | Y | N | Y
1850 | 2005-11-28 | BR | E-MIO | CIN | 1199 | 2005-11-28 | 804F6505 | 2010-06-01 | Dresser | Terre Haute South 1st St | 1 | 138 |  | 287 | Uprate 13868 conductor to 100C operating temperature from Dresser to South 1st St. New limit 1200A terminal equipment. |  | IN |  |  | 100 |  |  |  | Planned | 10000 | Engr |  |  |  | 2005-11-28 | MTEP06 |  |  | Y | N | Y
1851 | 2005-11-28 | BR | E-MIO | CIN | 1199 | 2005-11-28 | 804F6505 | 2010-06-01 | Terre Haute South 1st St | Terre Haute Water St | 1 | 138 |  | 287 | Uprate 13868 conductor to 100C operating temperature from South 1st St to Water St. New limit 1200A terminal equipment. |  | IN |  |  | 100 |  |  |  | Planned | 10000 | Engr |  |  |  | 2005-11-28 | MTEP06 |  |  | Y | N | Y
1852 | 2005-11-28 | BR | E-MIO | CIN | 1200 | 2005-11-28 | 702F6501 | 2010-06-01 | Speed |  | 3 | 345 | 138 | 520 | Upgrade 2000A 138kV breaker & switch and any other Bk3 limiting equipment. Replace any equipment that would limit the 345/138 xfr to less than the hot spot rating of 520 MVA. |  | IN |  |  | 100 |  |  |  | Planned | 173193.11 | Engr |  |  |  | 2005-11-28 | MTEP06 |  |  | Y | N | Y
1958 | 2006-03-27 | BR | E-MIO | CIN | 1245 | 2006-03-27 | 604G6616 | 2010-06-01 | Frankfort Jefferson | Potato Creek |  | 69 |  | 153 | 69178 Build 2.7 miles of 954 ACSR 69kV |  | IN |  |  | 100 |  |  |  | Planned |  |  |  | Y | [5 empty] | Y | N | Y
1959 | 2006-03-27 | BR | E-MIO | CIN | 1245 | 2006-03-27 | 602G6617 | 2010-06-01 | Potato Creek Switching Station |  |  | 69 |  |  | Construct 69kV switching station |  | IN |  |  | 100 |  |  |  | Planned |  |  |  | Y | [5 empty] | Y | N | Y
1982 | 2006-07-05 | DV | E-MIO | CIN | 1265 | 2006-07-05 | 502G6690 | 2010-06-01 | Geist 2 | Capacitor |  | 69 |  | 36 MVAR | Add a second 69kV 36MVAR cap bank at Geist |  | IN |  |  | 100 |  |  |  | Planned | 500000 | Plan |  | Y |  | 2006-07-05 |  | Jim Doell |  | Y | N | Y
1844 | 2005-11-28 | DV | E-MIO | CIN | 1194 | 2005-11-28 | X02P6411 | 2010-12-31 | Prescott | Capacitor |  | 69 |  | 43.2 MVAR | Add capacitor on 6976 line terminal |  | IN |  |  | 100 |  |  |  | Planned | 439844.75 | Engr | 1783414.67 |  |  | 2005-11-28 | MTEP06 |  |  | Y | N | Y
1312 | 2005-07-11 | BR | E-MIO | CIN | 845 | 2005-07-11 | AN | 2011-06-01 | Stillwell | transformer | 1 | 138 | 69 |  | Add new 138/69kV substation | N10 | OH | 0 | 0 | 100 |  |  |  | Planned | 5674746 | Engr |  | Y | [5 empty] | Y | N | Y
826 | 2005-07-11 | BR | E-MIO | CIN | 851 | 2005-07-11 | AT | 2011-06-01 | Lafayette Cumberland Ave | Laf AE Staley | 1 | 138 |  | 306 | 13806 reconductor with 954ACSR 100C 604F6347 | L9 | IN | 1.3 |  | 100 |  |  |  | Planned | 325000 | Planning MISO |  | Y |  |  | MTEP06 |  |  | Y | N | Y
1948 | 2006-03-27 | BR | E-MIO | CIN | 1242 | 2006-03-27 | 604G6544 | 2011-06-01 | Greentown | Peru SE |  | 230 |  | 478 | Uprate 23021 circuit to 100C operating temp |  | IN |  |  | 100 |  |  |  | Planned | 28403 | Engr |  | Y | [5 empty] | Y | N | Y
1945 | 2006-03-27 | BR | E-MIO | CIN | 1244 | 2006-03-27 | 802G6557 | 2011-06-01 | Cayuga 23013 Wave Trap | Frankfort |  | 230 |  | 797 | Replace 1600A wave trap with a 2000A wave trap. Increase line rating of the Cayuga to Frankfort 23013 line. |  | IN |  |  | 100 |  |  |  | Planned | 68733 | Engr |  | Y | [5 empty] | Y | N | Y
1946 | 2006-03-27 | BR | E-MIO | CIN | 1244 | 2006-03-27 | 602G6558 | 2011-06-01 | Frankfort 23013 Wave Trap | Cayuga |  | 230 |  | 797 | Replace 1600A wave trap with a 2000A wave trap. Increase line rating of the Cayuga to Frankfort 23013 line. |  | IN |  |  | 100 |  |  |  | Planned | 98827 | Engr |  | Y | [5 empty] | Y | N | Y
1947 | 2006-03-27 | BR | E-MIO | CIN | 1246 | 2006-03-27 | 602G6548 | 2011-06-01 | Five Points 23030 Wave Trap | Geist |  | 230 |  | 405 | Replace 800A wave trap with a 2000A wave trap. Increase line rating to Geist. |  | IN |  |  | 100 |  |  |  | Planned | 24038 | Engr |  | Y | [5 empty] | Y | N | Y
1950 | 2006-03-27 | BR | E-MIO | CIN | 1251 | 2006-03-27 | 502G6545 | 2011-06-01 | Noblesville 23008 Wave Trap | Carmel 146th St Jct |  | 230 |  | 405 | Replace 800A wave trap with a 2000A wave trap. Increase 230kV line rating to Carmel 146th St Jct. |  | IN |  |  | 100 |  |  |  | Planned | 24038 | Engr |  | Y | [5 empty] | Y | N | Y
1952 | 2006-03-27 | BR | E-MIO | CIN | 1253 | 2006-03-27 | 502G6547 | 2011-06-01 | Noblesville 23007 Wave Trap | Geist |  | 230 |  | 405 | Replace 800A wave trap with a 2000A wave trap. Increase line rating to Geist. |  | IN |  |  | 100 |  |  |  | Planned | 24038 | Engr |  | Y | [5 empty] | Y | N | Y
1980 | 2006-07-05 | BR | E-MIO | CIN | 1263 | 2006-07-05 | EDWPIGCC | 2011-06-01 | Edwardsport IGCC | [5 empty] | Provide 345 and/or 138 kV interconnection for Edwardsport IGCC plant. |  | IN |  |  |  | 100 |  |  | Proposed |  |  |  | N |  | 2006-07-05 |  | Jim Doell | G#? | Y | N | Y |  | Gen Int
1981 | 2006-07-05 | BR | E-MIO | CIN | 1264 | 2006-07-05 | 702G6714 | 2011-06-01 | Speed |  |  | 345 | 138 | 717 | Replace existing 345/138 transformer at Speed with a new transformer rated at 3,000A or higher. |  | IN |  |  | 100 |  |  |  | Proposed | 5000000 | Plan | 11267823 | N |  | 2006-07-05 |  | Jim Doell |  | Y | N | Y
3071 | 2005-11-28 | DV | E-MIO | CIN | 834 | 2005-07-11 | AC | 2012-06-01 | Kingman | Capacitor |  | 69 |  | 7.2 MVAR | Add capacitor | L9 | IN |  |  | 100 |  |  |  | Planned | 500000 | Plan |  | Y | [5 empty] | Y | N | Y
820 | 2005-07-11 | BR | E-MIO | CIN | 841 | 2005-07-11 | AJ | 2013-06-01 | Westwood Bk1 | transformer | 1 | 345 | 138 | 412.9 | Replace 1200A 138kV equipment with 2000A to allow full xfr rating. | L9 | IN |  |  | 100 |  |  |  | Planned | 554000 | Planning MISO |  | Y |  |  | MTEP06 |  |  | Y | N | Y
819 | 2005-07-11 | DV | E-MIO | CIN | 840 | 2005-07-11 | AI | 2014-06-01 | Rushville | Capacitor |  | 69 |  | 14.4 MVAR | Add capacitor | M10 | IN |  |  | 100 |  |  |  | Planned | 500000 | Plan |  | Y |  |  | MTEP06 |  |  | Y | N | Y
1957 | 2006-03-27 | DV | E-MIO | CIN | 1249 | 2006-03-27 | 602G6621 | 2014-12-31 | Frankfort 230 | Capacitor |  | 69 |  | 36 MVAR | Install 36 MVAR 69kV capacitor |  | IN |  |  | 100 |  |  |  | Planned |  |  |  | Y | [5 empty] | Y | N | Y
828 | 2005-07-11 | BR | E-MIO | CIN | 853 | 2005-07-11 | AV | 2015-06-01 | West Lafayette | Cumberland Ave | 1 | 138 |  | 306 | 13806 reconductor with 954ACSR 100C 604F6325 | L9 | IN | 2 |  | 100 |  |  |  | Planned | 646000 | Planning MISO |  | Y |  |  | MTEP06 |  |  | Y | N | Y
807 | 2005-09-14 | BR | N-NM | DPC/XEL | 584 | 2005-06-15 |  | 2008-06-01 | Genoa | Coulee | 1 | 161 |  | 304 |  | E13 | WI | 18.7 |  | 100 |  |  |  | Planned | 4057132 |  |  |  | reused MTEP03 number | 2004-11-09 | MTEP05 |  |  | Y | Y | Y
648 | 2005-08-31 | BR | N-NM | EEI (MP) | 1025 | 2005-08-31 | Mesaba Energy | 2010-10-01 | Diamond Lake | Blackberry | 2 | 230 |  | 600 | double circuit with existing 115 kV lines | I4 | MN |  | 18.5 |  | 100 |  |  | Proposed | 12300000 | Planning MISO |  |  | Mesaba Energy Project |  |  |  | G519, G477 | Y | Y | N |  | Network
647 | 2005-08-31 | BR | N-NM | EEI (MP) | 1025 | 2005-08-31 | Mesaba Energy | 2010-10-01 | Diamond Lake | Blackberry | 1 | 230 |  | 600 | double circuit structures | I4 | MN | 4 | 6 |  | 100 |  |  | Proposed | 6800000 | Planning MISO |  |  | Mesaba Energy Project |  |  |  | G519, G477 | Y | Y | N |  | Network
649 | 2005-08-31 | BR | N-NM | EEI (MP) | 1025 | 2005-08-31 | Mesaba Energy | 2012-10-01 | Diamond Lake | Blackberry | 3 | 230 |  | 600 | add 2nd circuit to ckt 1 | I4 | MN | 4 | 6 |  | 100 |  |  | Proposed | 3600000 | Planning MISO |  |  | Mesaba Energy Project |  |  |  | G519, G477 | Y | Y | N |  | Network
1720 | 2005-11-18 | GEN | East | FE | 1070 | 2005-11-18 |  | 2003-05-01 |  | generator |  |  |  | 700 | new generator |  | OH |  |  |  | 100 |  |  | Under Construction | [8 empty] | F33 | Y | N | Y |  | Generator
1284 | 2006-06-29 | BR | E-MIO | FE | 616 | 2006-03-14 |  | 2007-06-01 | Crissinger | Tangy | 1 | 138 |  | 275 MVA |  | O8 | OH | 23 |  | 100 |  |  |  | Planned | 2713000 |  |  |  |  | 2005-01-12 |  | Phil Bowers |  | Y | N | Y
1283 | 2006-06-29 | BR | E-MIO | FE | 615 | 2005-07-11 |  | 2007-12-01 | Galion 345-138 kV | transformer prep. |  | 345 | 138 |  | Protection upgrades to separate existing transformers, so they don't trip together | O8 | OH |  |  | 100 |  |  |  | Planned | 1815566 |  |  |  |  | 2005-01-12 |  | Phil Bowers |  | Y | N | Y
899 | 2006-06-29 | BR | E-MIO | FE | 890 | 2005-07-06 |  | 2008-06-01 | North Medina new 345-115 kV | substation | 4 | 345 | 138 |  | Add a new 345/138kV substation at the junction of the Star-Carlisle 345kV and Star-West Akron #2 138kV lines | O8 | OH |  |  | 100 |  |  |  | Planned | 8405000 |  |  |  |  | 2005-07-06 | MTEP06 | Phil Bowers |  | Y | N | Y
1711 | 2005-11-18 | GEN | East | FE | 1061 | 2005-11-18 |  |  |  | generator |  |  |  | 50 | new generator |  | OH |  |  |  | 100 |  |  | Planned | [8 empty] | F23 | Y | N | Y |  | Generator
1712 | 2005-11-18 | GEN | East | FE | 1062 | 2005-11-18 |  |  |  | generator |  |  |  | 50 | new generator |  | OH |  |  |  | 100 |  |  | Planned | [8 empty] | F24 | Y | N | Y |  | Generator
1782 | 2005-11-18 | GEN | East | FE | 1132 | 2005-11-18 |  |  |  | generator |  |  |  | 6 | new generator |  | OH |  |  |  | 100 |  |  | Under Construction | [8 empty] | F221 | Y | N | Y |  | Generator
1715 | 2005-11-18 | GEN | West | GRE | 1065 | 2005-11-18 |  | 2003-04-01 |  | generator | 1 |  |  | 55 | new generator |  | MN |  |  |  | 100 |  |  | Planned |  |  |  |  | 60374 |  |  |  | G034 | Y | N | Y |  | Generator
3022 | 2005-01-25 | DV | N-NM | GRE | 753 | 2005-06-15 |  | 2005-06-01 | Hubbard | Capacitor |  | 115 |  | 27 Mvar |  | G4 | MN |  |  | 100 |  |  |  | Planned | 594661 | [8 empty] | Y | Y | Y
901 | 2005-06-27 | BR | N-NM | GRE | 892 | 2005-06-27 |  | 2005-10-01 | Parkwood 115-69 kV | transformer | 2 | 115 | 69 | 140 | add 2nd transformer | TC detail | MN |  |  | 100 |  |  |  | Planned | 1845000 | Planning MISO |  |  |  | 2005-06-27 | MTEP06 |  |  | Y | Y | Y
1790 | 2005-11-18 | GEN | West | GRE | 1140 | 2005-11-18 |  | 2005-12-01 | East Ridge | generator |  |  |  | 10 | new generator |  | MN |  |  |  | 100 |  |  | Planned |  |  |  |  | 62710 |  |  |  | G272 | Y | N | Y |  | Generator
1082 | 2005-01-25 | BR | N-NM | GRE | 597 | 2005-06-15 |  | 2006-05-01 | Plymouth | Elm Creek | 1 | 115 |  | 300 |  | TC detail | MN | 9.5 | 2.5 | 100 |  |  |  | Planned | 9000000 | [8 empty] | Y | Y | Y
1081 | 2005-01-25 | BR | N-NM | GRE | 597 | 2005-06-15 |  | 2006-05-01 | Parkers Lake | Plymouth | 1 | 115 |  | 300 |  | TC detail | MN |  | 4.3 | 100 |  |  |  | Planned | 3660000 | [8 empty] | Y | Y | Y
900 | 2005-06-27 | BR | N-NM | GRE | 891 | 2005-06-27 |  | 2006-09-01 | Elk River 230-69 kV | transformer | 2 | 230 | 69 | 187 | add 2nd transformer | TC detail | MN |  |  | 100 |  |  |  | Planned | 2704000 | Planning MISO |  |  |  | 2005-06-27 | MTEP06 |  |  | Y | Y | Y
1078 | 2005-01-25 | BR | N-NM | GRE | 600 | 2005-06-15 |  | 2006-12-31 | Baxter | Southdale | 1 | 115 |  | 224 |  | H5 | MN | 1.3 | 6.5 | 100 |  |  |  | Planned | 3500000 |  | 18864000 | [6 empty] | Y | Y | Y
752 | 2005-06-27 | BR | N-NM | GRE | 1026 | 2005-06-27 | A125, A130 | 2007-03-01 | Linwood 230-69 kV | transformer | 1 | 230 | 69 | 112 |  | TC detail | MN |  |  | 100 |  |  |  | Planned | 5000000 |  |  |  | no PrjID |  |  |  | A125, A130 | Y | Y | Y |  |  | Y
1076 | 2005-11-28 | BR | N-NM | GRE | 596 | 2005-06-15 |  | 2007-05-01 | Vermillion River | Empire | 1 | 115 |  | 200 |  | TC detail | MN |  | 6 | 100 |  |  |  | Planned | 2750000 |  |  |  | There has been a lawsuit filed on proposed route |  |  |  |  | Y | Y | Y
641 | 2005-06-30 | BR | N-NM | GRE | 601 | 2005-06-15 |  | 2008-06-01 | Mud Lake | Wilson Lake | 1 | 115 |  | 142 |  | H5 | MN | 12 |  | 100 |  |  |  | Planned | 6000000 | [8 empty] | Y | Y | Y
753 | 2005-11-28 | BR | N-NM | GRE | 599 | 2005-06-15 |  | 2009-06-01 | Crooked Lake | Enterprise Park | 1 | 115 |  | 142 |  | TC detail | MN |  | 3.5 | 100 |  |  |  | Planned | 3600000 |  |  |  | 2 line upgrades will allow delay in heavy construction schedule | 2004-08-31 |  |  |  | Y | Y | Y
640 | 2004-12-23 | BR | N-NM | GRE | 1018 | 2004-12-23 |  | 2011-06-01 | Little Falls | Pierz (operated 34 kV) | 1 | 115 |  | 196 |  | H5 | MN | 9 |  | 100 |  |  |  | Proposed | 900000 | Planning MISO |  |  | 115 kv line operated at 34.5. Is line converted to 115 kV op at this time? |  |  |  |  | Y | Y | Y
802 | 2005-01-25 | BR | N-NM | GRE | 602 | 2005-06-15 |  | 2012-06-01 | Brownton | McLeod | 1 | 115 |  |  |  | H6 | MN |  | 9 | 100 |  |  |  | Planned | 4675000 | [8 empty] | Y | Y | Y
1104 | 2005-11-28 | BR | N-NM | GRE/MPC/XEL/OTP/MP/WAPA | 286 | 2005-07-29 | CAPX Group 1 | 2012-07-01 | Alexandria | Benton County | 1 | 345 |  | 720 | Add a new 345 kV line from Benton County to Alexandria Switching Station | G5 | MN |  | 62.5 | 100 |  |  |  | Proposed | 61069477 | Planning |  |  | 345 kV CON process and the following route acquisition may result in delays for construction timeline (adjusted schedule) |  |  |  |  | Y | Y | Y
1105 | 2005-11-28 | BR | N-NM | GRE/MPC/XEL/OTP/MP/WAPA | 287 | 2005-07-29 | CAPX Group 1 | 2012-07-01 | Maple River | Alexandria | 1 | 345 |  | 720 | Add a new 345 kV line from Alexandria Switching Station to Maple River substation | F4 | MN/ND |  | 100 | 100 |  |  |  | Proposed | 64283661 | Planning |  |  | 345 kV CON process and the following route acquisition may result in delays for construction timeline (adjusted schedule) |  |  |  |  | Y | Y | Y
1276 | 2005-01-03 | BR | N-NM | GRE/OTP | 1033 | 2005-01-03 |  | 2011-06-01 | Silver Lake 230/41.6 kV | transformer | 1 | 230 | 41.6 | 50 |  | G5 |  |  |  | 100 |  |  |  | Planned | 1840000 |  |  |  | Long-term Planned | 2005-01-03 |  |  |  | Y | Y | N
801 | 2005-07-19 | BR | N-NM | GRE/XEL | 603 | 2005-06-15 |  | 2011-06-01 | Alexandria | West St. Cloud | 1 | 115 |  | 310 |  | G5-H5 | MN |  | 75 | 100 |  |  |  | Proposed | 36954688 | [8 empty] | Y | Y | Y
1893 | 2006-01-25 | BR | N-NM | GRE/XEL | 1203 | 2006-01-25 | SW MN - TC EHV | 2011-06-01 | Lyon County | Transfomer | 1 | 345 | 115 | 448 |  |  | MN | [6 empty] | Proposed | 6000000 |  |  |  |  | 2006-01-25 |  |  |  | Y | Y | Y
1881 | 2006-01-25 | BR | N-NM | GRE/XEL | 1203 | 2006-01-25 | SW MN - TC EHV | 2011-06-01 | Brookings County | Lyon County 345 kV | 1 | 345 |  | 2066 |  |  | SD |  | 49 |  |  |  |  | Proposed | 39200000 |  |  |  |  | 2006-01-25 |  |  |  | Y | Y | Y
1883 | 2006-01-25 | BR | N-NM | GRE/XEL | 1203 | 2006-01-25 | SW MN - TC EHV | 2011-06-01 | Lyon County | Franklin | 2 | 345 |  | 2066 |  |  | MN |  | 44 |  |  |  |  | Proposed | 17600000 |  |  |  |  | 2006-01-25 |  |  |  | Y | Y | Y
1885 | 2006-01-25 | BR | N-NM | GRE/XEL | 1203 | 2006-01-25 | SW MN - TC EHV | 2011-06-01 | Franklin | Helena | 2 | 345 |  | 2066 |  |  | MN |  | 67 |  |  |  |  | Proposed | 26800000 |  |  |  |  | 2006-01-25 |  |  |  | Y | Y | Y
1886 | 2006-01-25 | BR | N-NM | GRE/XEL | 1203 | 2006-01-25 | SW MN - TC EHV | 2011-06-01 | Helena | Lake Marion | 1 | 345 |  | 2066 |  |  | MN |  | 16 |  |  |  |  | Proposed | 12800000 |  |  |  |  | 2006-01-25 |  |  |  | Y | Y | Y
1887 | 2006-01-25 | BR | N-NM | GRE/XEL | 1203 | 2006-01-25 | SW MN - TC EHV | 2011-06-01 | Lake Marion | Hampton Corner | 1 | 345 |  | 2066 |  |  | MN |  | 18 |  |  |  |  | Proposed | 14400000 |  |  |  |  | 2006-01-25 |  |  |  | Y | Y | Y
1888 | 2006-01-25 | BR | N-NM | GRE/XEL | 1203 | 2006-01-25 | SW MN - TC EHV | 2011-06-01 | Lyon County | Hazel | 1 | 345 |  | 2066 |  |  | MN |  | 22 |  |  |  |  | Proposed | 18480000 |  |  |  |  | 2006-01-25 |  |  |  | Y | Y | Y
1889 | 2006-01-25 | BR | N-NM | GRE/XEL | 1203 | 2006-01-25 | SW MN - TC EHV | 2011-06-01 | Hazel | Minnesota Valley | 1 | 345 |  | 2066 |  |  | MN |  | 8 |  |  |  |  | Proposed | 3600000 |  |  |  |  | 2006-01-25 |  |  |  | Y | Y | Y
1890 | 2006-01-25 | BR | N-NM | GRE/XEL | 1203 | 2006-01-25 | SW MN - TC EHV | 2011-06-01 | Brookings County | Yankee | 2 | 115 |  | 310 |  |  | SD |  | 14 |  |  |  |  | Proposed | 7000000 |  |  |  |  | 2006-01-25 |  |  |  | Y | Y | Y
1892 | 2006-01-25 | BR | N-NM | GRE/XEL | 1203 | 2006-01-25 | SW MN - TC EHV | 2011-06-01 | Brookings County | Transfomer | 2 | 345 | 115 | 448 |  |  | SD | [6 empty] | Proposed | 6000000 |  |  |  |  | 2006-01-25 |  |  |  | Y | Y | Y
1882 | 2006-01-25 | BR | N-NM | GRE/XEL | 1203 | 2006-01-25 | SW MN - TC EHV | 2011-06-01 | Lyon County | Franklin | 1 | 345 |  | 2066 |  |  | MN |  | 44 |  |  |  |  | Proposed | 35200000 |  |  |  |  | 2006-01-25 |  |  |  | Y | Y | Y
1894 | 2006-01-25 | BR | N-NM | GRE/XEL | 1203 | 2006-01-25 | SW MN - TC EHV | 2011-06-01 | Lake Marion | Transfomer | 1 | 345 | 115 | 448 |  |  | MN | [6 empty] | Proposed | 6000000 |  |  |  |  | 2006-01-25 |  |  |  | Y | Y | Y
1895 | 2006-01-25 | BR | N-NM | GRE/XEL | 1203 | 2006-01-25 | SW MN - TC EHV | 2011-06-01 | Hazel | Transfomer | 1 | 345 | 230 | 336 |  |  | MN | [6 empty] | Proposed | 6000000 |  |  |  |  | 2006-01-25 |  |  |  | Y | Y | Y
1896 | 2006-01-25 | BR | N-NM | GRE/XEL | 1203 | 2006-01-25 | SW MN - TC EHV | 2011-06-01 | Hazel | Transfomer | 2 | 345 | 230 | 336 |  |  | MN | [6 empty] | Proposed | 4000000 |  |  |  |  | 2006-01-25 |  |  |  | Y | Y | Y
1897 | 2006-01-25 | BR | N-NM | GRE/XEL | 1203 | 2006-01-25 | SW MN - TC EHV | 2011-06-01 | Franklin | Transfomer | 1 | 115 | 69 | 70 | Upgrade 47 MVA to 70 MVA |  | MN | [6 empty] | Proposed | 4000000 |  |  |  |  | 2006-01-25 |  |  |  | Y | Y | Y
1898 | 2006-01-25 | BR | N-NM | GRE/XEL | 1203 | 2006-01-25 | SW MN - TC EHV | 2011-06-01 | Morris | Transfomer | 2 | 230 | 115 | 150 | Upgrade 100 MVA to 150 MVA |  | MN | [6 empty] | Proposed | 4000000 |  |  |  |  | 2006-01-25 |  |  |  | Y | Y | Y
1899 | 2006-01-25 | BR | N-NM | GRE/XEL | 1203 | 2006-01-25 | SW MN - TC EHV | 2011-06-01 | Willmar | Transfomer | 2 | 115 | 69 | 112 |  |  | MN | [6 empty] | Proposed | 3000000 |  |  |  |  | 2006-01-25 |  |  |  | Y | Y | Y
1891 | 2006-01-25 | BR | N-NM | GRE/XEL | 1203 | 2006-01-25 | SW MN - TC EHV | 2011-06-01 | Brookings County | Toronto | 1 | 345 |  | 2066 |  |  | SD |  | 20 |  |  |  |  | Proposed | 7000000 |  | Xcel and GRE |  | Xcel | 2006-01-25 |  |  |  | Y | Y | Y
1884 | 2006-01-25 | BR | N-NM | GRE/XEL | 1203 | 2006-01-25 | SW MN - TC EHV | 2011-06-01 | Franklin | Helena | 1 | 345 |  | 2066 |  |  | MN |  | 67 |  |  |  |  | Proposed | 53600000 |  | 277411226.9473 |  | 242411226.9473 | 2006-01-25 |  |  |  | Y | Y | Y
179 | 2003-06-03 | BR | E-MIO | HE | 204 | 2005-06-15 |  | 2009-06-01 | North Charleston | Tapline w/ substation | 1 | 138 |  |  |  | M10 | IN |  | 0.1 | 100 |  |  |  | Proposed | 900000 | [5 empty] | MTEP03 |  |  | Y | N | Y
171 | 2003-06-03 | BR | E-MIO | HE | 204 | 2005-06-15 |  | 2009-06-01 | Batesville | Tapline w/ substation | 1 | 138 |  |  |  | M10 | IN |  | 0.5 | 100 |  |  |  | Proposed | 950000 | [5 empty] | MTEP03 |  |  | Y | N | Y
903 | 2006-06-26 | DV | E-MIO | IPL | 894 | 2006-06-26 | IPL-03 | 2006-07-01 | Pike | Capacitor |  | 138 |  | 150 MVAR | New 150 MVAR Capacitor Bank | M9 | IN |  |  | 100 |  |  |  | Planned | 1613000 | Planning MISO |  |  |  | 2005-07-06 | MTEP06 |  |  | Y | N | Y
178 | 2005-11-28 | BR | E-MIO | IPL | 40 | 2005-11-17 | IPL-05 | 2007-06-01 | Cumberland | Julietta | 1 | 138 |  | 286 MVA | New 138kV Line | M9 | IN |  | 4.55 | 100 |  |  |  | Planned | 866172.7854 |  |  |  | Project delayed due to Growth projections |  |  |  |  | Y | N | Y
177 | 2005-11-28 | BR | E-MIO | IPL | 40 | 2005-11-17 | IPL-05 | 2007-06-01 | Indian Creek | Julietta | 1 | 138 |  | 286 MVA | New 138kV Line | M9 | IN |  | 5 | 100 |  |  |  | Planned | 951838.2257 |  |  |  | Project delayed due to Growth projections |  |  |  |  | Y | N | Y
902 | 2006-06-26 | DV | E-MIO | IPL | 893 | 2005-07-06 | IPL-02 | 2007-06-01 | North | Capacitor |  | 138 |  | 150 MVAR | Increase Capacitor Size To 150 MVAR | M9 | IN |  |  | 100 |  |  |  | Planned | 1613000 | Planning MISO |  |  |  | 2005-07-06 | MTEP06 |  |  | Y | N | Y
905 | 2006-06-26 | DV | E-MIO | IPL | 895 | 2006-06-26 | IPL-04 | 2007-07-01 | North | Breaker |  | 138 |  | 245 MVA | New 2000 Amp Breaker | M9 | IN |  |  | 100 |  |  |  | Planned | 354000 | Planning MISO |  |  | North to Northeast 138 | 2005-07-06 | MTEP06 |  |  | Y | N | Y
904 | 2006-06-26 | DV | E-MIO | IPL | 895 | 2006-06-26 | IPL-04 | 2007-07-01 | North | Breaker |  | 138 |  | 245 MVA | New 2000 Amp Breaker | M9 | IN |  |  | 100 |  |  |  | Planned | 354000 | Planning MISO | 4139011.0111 |  | Georgetown to North 138 | 2005-07-06 | MTEP06 |  |  | Y | N | Y
907 | 2006-02-16 | BR | E-MIO | IPL | 897 | 2005-07-06 | IPL-07 | 2012-06-01 | Thompson 345-138 kV | transformer | 1 | 345 | 138 | 400 MVA | New 345/138kV Autotransformer | M9 | IN |  |  | 100 |  |  |  | Proposed | 4500000 | Planning |  |  |  | 2005-07-06 | MTEP06 | M Kempker |  | Y | N | Y
758 | 2006-03-06 | BR | E-MIO | ITC | 503 | 2005-08-10 | 503 | 2006-12-31 | Wixom 345/230 | transformer | 1 | 345 | 230 | 782 |  | M9 | MI | 0 | 0 |  |  | 50 | 50 | Planned | 5000000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
757 | 2006-03-06 | BR | E-MIO | ITC | 503 | 2005-08-10 | 503 | 2006-12-31 | Wixom 230 | Quaker 230 | 1 | 230 |  | 657 |  | M9 | MI | 5 | 4.3 |  |  | 50 | 50 | Planned | 2300000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
759 | 2006-03-06 | BR | E-MIO | ITC | 503 | 2005-08-10 | 503 | 2006-12-31 | Quaker 230-120 kV | transformer | 1 | 230 | 120 | 634 |  | M9 | MI | 0 | 0 |  |  | 50 | 50 | Planned | 1500000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
765 | 2006-03-06 | BR | E-MIO | ITC | 509 | 2005-08-10 | 509 | 2006-12-31 | Lenox 120 | Victor 120 | 1 | 120 |  | 313 |  | O7 | MI | 1.08 |  |  |  |  | 100 | Planned | 1300000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
768 | 2006-03-06 | BR | E-MIO | ITC | 509 | 2005-08-10 | 509 | 2006-12-31 | Lenox 120 | Grayling 1 120 | 1 | 120 |  | 313 |  | O7 | MI | 10.8 |  |  |  |  | 100 | Planned | 1300000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
762 | 2006-03-06 | BR | E-MIO | ITC | 509 | 2005-08-10 | 509 | 2006-12-31 | Lenox 345 | Belle River 345 | 1 | 345 |  | 2002 |  | O7 | MI | 19.1 |  |  |  |  | 100 | Planned | 1750000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
767 | 2006-03-06 | BR | E-MIO | ITC | 509 | 2005-08-10 | 509 | 2006-12-31 | Lenox 120 | Grayling 2 120 | 1 | 120 |  | 313 |  | O7 | MI | 10.8 |  |  |  |  | 100 | Planned | 1300000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
761 | 2006-03-06 | BR | E-MIO | ITC | 509 | 2005-08-10 | 509 | 2006-12-31 | Lenox 345 | Jewel 345 | 1 | 345 |  | 2007 |  | O7 | MI | 8.7 |  |  |  |  | 100 | Planned | 1750000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
766 | 2006-03-06 | BR | E-MIO | ITC | 509 | 2005-08-10 | 509 | 2006-12-31 | Lenox 120 | Augusta Tap 120 | 1 | 120 |  | 343 |  | O7 | MI | 4.98 |  |  |  |  | 100 | Planned | 1300000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
763 | 2006-03-06 | BR | E-MIO | ITC | 509 | 2005-08-10 | 509 | 2006-12-31 | Lenox 345-120 kV | transformer | 1 | 345 | 120 | 500 |  | O7 | MI |  | 0 |  |  |  | 100 | Planned | 5000000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
764 | 2006-03-06 | BR | E-MIO | ITC | 509 | 2005-08-10 | 509 | 2006-12-31 | Lenox 120 | St Clair 120 | 1 | 120 |  | 312.8 |  | O7 | MI | 19.5 |  |  |  |  | 100 | Planned | 1300000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
2100 | 2005-11-28 | DV | E-MIO | ITC | 578 | 2005-08-10 | 578 | 2006-12-31 | Wyatt | DVAR |  | 120 |  | 30 Mvar |  | N9 | MI |  |  | 100 |  |  |  | Planned | 3500000 |  |  |  | project redefined |  |  | Bad Axe to Wyatt |  | Y | N | Y
1377 | 2006-07-05 | BR | E-MIO | ITC | 686 | 2005-08-10 | ITC7 | 2006-12-31 | Majestic 120 kV | Madrid 120 kV | 2 | 120 |  | 445 |  | N7 | MI | 15.9 |  | 100 |  |  |  | Planned | 1800000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
1378 | 2006-07-05 | BR | E-MIO | ITC | 686 | 2005-08-10 | ITC7 | 2006-12-31 | Majestic 345/120 kV | transformer | 1 | 345 | 120 | 681 |  | N7 | MI | 0 | 0 | 100 |  |  |  | Planned | 5000000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
928 | 2006-07-05 | BR | E-MIO | ITC | 904 | 2005-08-10 | ITC14 | 2006-12-31 | Wyatt 120 kV | Sandusky 120 kV | 1 | 120 |  | 150 |  | N9 | MI | 29.3 | [5 empty] | Planned | 1000000 |  |  |  |  | 2005-07-08 | MTEP06 | ITC - Jeff Wyman |  | Y | N | Y
927 | 2006-07-05 | BR | E-MIO | ITC | 904 | 2005-08-10 | ITC14 | 2006-12-31 | Wyatt 120 kV | Seaside 120 kV | 1 | 120 |  | 222 |  | N9 | MI | 15.7 | [5 empty] | Planned | 1000000 |  |  |  |  | 2005-07-08 | MTEP06 | ITC - Jeff Wyman |  | Y | N | Y
925 | 2006-07-05 | BR | E-MIO | ITC | 904 | 2005-08-10 | ITC14 | 2006-12-31 | Wyatt 120 kV | Bad Ax 120 kV | 1 | 120 |  | 150 |  | N9 | MI | 2.6 | [5 empty] | Planned | 1000000 |  |  |  |  | 2005-07-08 | MTEP06 | ITC - Jeff Wyman |  | Y | N | Y
926 | 2006-07-05 | BR | E-MIO | ITC | 904 | 2005-08-10 | ITC14 | 2006-12-31 | Wyatt 120 kV | Harbor Beach 120 kV | 1 | 120 |  | 150 |  | N9 | MI | 17.2 | [5 empty] | Planned | 1000000 |  |  |  |  | 2005-07-08 | MTEP06 | ITC - Jeff Wyman |  | Y | N | Y
929 | 2006-07-05 | BR | E-MIO | ITC | 905 | 2005-08-10 | ITC15 | 2006-12-31 | Bunce Creek 120 kV | Wabash 120 kV 2 | 2 | 120 |  | 299 |  | N9 | MI | 0.1 | 0 | 50 |  |  | 50 | Planned | 1166666 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
930 | 2006-07-05 | BR | E-MIO | ITC | 905 | 2005-08-10 | ITC15 | 2006-12-31 | Bunce Creek 120 kV | Menlo 120 kV | 1 | 120 |  | 152 |  | N9 | MI | 0.1 | 0 | 50 |  |  | 50 | Planned | 1166666 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
931 | 2006-07-05 | BR | E-MIO | ITC | 905 | 2005-08-10 | ITC15 | 2006-12-31 | Bunce Creek 120 kV | Cypress 120 kV | 1 | 120 |  | 313 |  | N9 | MI | 0.1 | 0 | 50 |  |  | 50 | Planned | 1166668 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
1583 | 2006-07-05 | BR | E-MIO | ITC | 1011 | 2006-07-05 | ITC22 | 2006-12-31 | Genoa 120 kV | Durant 120 kV | 1 | 120 |  | 343 |  | N7 | MI |  | 8.5 | 100 |  |  |  | Planned | 5500000 |  |  |  |  | 2005-08-10 | MTEP06 | ITC - Jeff Wyman |  | Y | N | Y
1584 | 2006-07-05 | BR | E-MIO | ITC | 1011 | 2006-07-05 | ITC22 | 2006-12-31 | Placid 120 kV | Durant 120 kV | 1 | 120 |  | 343 |  | N7 | MI | 16.7 |  | 100 |  |  |  | Planned | 3500000 |  |  |  |  | 2005-08-10 | MTEP06 | ITC - Jeff Wyman |  | Y | N | Y
1585 | 2006-07-05 | BR | E-MIO | ITC | 1011 | 2006-07-05 | ITC22 | 2006-12-31 | Placid 120 kV | Proud 120 kV | 1 | 120 |  | 343 |  | N7 | MI | 14.3 |  | 100 |  |  |  | Planned | 3500000 | 54100000 |  |  |  | 2005-08-10 | MTEP06 | ITC - Jeff Wyman |  | Y | N | Y
760 | 2005-07-08 | BR | E-MIO | ITC | 503 | 2005-08-10 | 503 | 2007-05-30 | Hancock 120 | Southfield 120 | 1 | 120 |  | 244 |  | N7 | MI | 3.7 |  |  |  | 50 | 50 | Planned | 1200000 | [8 empty] | Y | N | Y
773 | 2005-07-08 | BR | E-MIO | ITC | 518 | 2005-08-10 | 518 | 2007-05-30 | Golf 120 | Macomb 120 #2 | 2 | 120 |  | 291 |  | O7 | MI | 3.2 |  |  |  |  | 100 | Planned | 1600000 | [8 empty] | Y | N | Y
771 | 2005-07-08 | BR | E-MIO | ITC | 518 | 2005-08-10 | 518 | 2007-05-30 | Golf 120 | Houston 2 120 | 1 | 120 |  | 313 |  | O7 | MI | 17.3 |  |  |  |  | 100 | Planned | 1200000 | [8 empty] | Y | N | Y
770 | 2005-07-08 | BR | E-MIO | ITC | 518 | 2005-08-10 | 518 | 2007-05-30 | Golf 120 | Boyne 120 | 1 | 120 |  | 290 |  | O7 | MI | 4.2 | 0.64 |  |  |  | 100 | Planned | 1200000 | [8 empty] | Y | N | Y
953 | 2006-07-05 | BR | E-MIO | ITC | 911 | 2005-08-10 | ITC21 | 2007-05-30 | Placid 345 kV | transformer | 2 | 345 | 120 | 700 |  | M9 | MI |  |  | 100 |  |  |  | Planned | 10000000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
1582 | 2005-08-10 | BR | E-MIO | ITC | 1012 | 2005-08-10 | zz | 2007-05-30 | Wayne 120 kV | Newburg 120 kV | 3 | 120 | 120 | 343 |  |  | MI |  | 2.8 |  |  |  |  | Proposed | 1200000 |  |  |  |  | 2005-08-10 | MTEP06 |  |  | Y | N | Y
1822 | 2005-11-18 | GEN | East | ITC | 1172 | 2005-11-18 |  | 2007-09-30 | Fermi plant | generator |  |  |  | 159 | increase generator capacity |  | MI |  |  |  | 100 |  |  | Planned | [8 empty] | G350 | Y | N | Y |  | Generator
774 | 2006-07-05 | BR | E-MIO | ITC | 586 | 2005-08-10 |  | 2007-12-31 | Stephens 120 | Erin 120 | 3 | 120 |  | 290 |  | O7 | MI | 4.7 |  | 100 |  |  |  | Planned | 34000000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
1382 | 2006-07-05 | BR | E-MIO | ITC | 686 | 2005-08-10 | ITC7 | 2007-12-31 | Majestic 120 kV | Phoenix 120 kV | 1 | 120 |  | 313 |  | N7 | MI | 7.4 | 9.2 | 100 |  |  |  | Planned | 3500000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
1381 | 2006-07-05 | BR | E-MIO | ITC | 686 | 2005-08-10 | ITC7 | 2007-12-31 | Majestic 120 kV | Lark 120 kV | 1 | 120 |  | 313 |  | N7 | MI | 2.6 | 9.2 | 100 |  |  |  | Planned | 2700000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
952 | 2006-07-05 | BR | E-MIO | ITC | 910 | 2005-08-10 | ITC20 | 2007-12-31 | Coventry 230 kV | Cody 230kV | 1 | 230 |  | 657 |  | N7 | MI | 6.6 |  | 100 |  |  |  | Planned | 8000000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
951 | 2006-07-05 | BR | E-MIO | ITC | 910 | 2005-08-10 | ITC20 | 2007-12-31 | Cody 230/120 kV | transformer | 1 | 230 | 120 | 693 |  | N7 | MI |  |  | 100 |  |  |  | Planned | 4000000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
950 | 2006-07-05 | BR | E-MIO | ITC | 910 | 2005-08-10 | ITC20 | 2007-12-31 | Coventry 345/230 | transformer | 1 | 345 | 230 | 782 |  | N7 | MI |  |  | 100 |  |  |  | Planned | 5000000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
1581 | 2006-07-05 | BR | E-MIO | ITC | 910 | 2005-08-10 | ITC20 | 2007-12-31 | Madrid 345 kV | Blackfoot 345 kV | 1 | 345 |  | 1793 |  | N7 | MI | [6 empty] | Planned | 3000000 | Planning MISO | 76600000 |  |  | 2005-08-10 | MTEP06 | ITC - Jeff Wyman |  | Y | N | Y
917 | 2005-07-08 | BR | E-MIO | ITC | 900 | 2005-08-10 | aa | 2008-05-30 | Hager 120 kV | Hines 120 kV | 1 | 120 |  | 347 |  | N7 | MI | 5.4 |  | 100 |  |  |  | Proposed | 1100000 |  |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1579 | 2005-08-10 | BR | E-MIO | ITC | 908 | 2005-08-10 | ii | 2008-05-30 | Lulu | Monroe 1-2 | 1 | 345 |  | 2000 |  |  | MI | 12.1 | 3 |  |  |  |  | Planned | 4500000 |  |  |  |  | 2005-08-10 | MTEP06 |  |  | Y | N | Y
1580 | 2005-08-10 | BR | E-MIO | ITC | 908 | 2005-08-10 | ii | 2008-05-30 | Lemoyne | Monroe 3-4 | 1 | 345 |  | 2000 |  |  | MI | 33.1 | 3 |  |  |  |  | Planned | 4500000 |  |  |  |  | 2005-08-10 | MTEP06 |  |  | Y | N | Y
938 | 2005-08-10 | BR | E-MIO | ITC | 908 | 2005-08-10 | ii | 2008-05-30 | Lulu | Allen Junction | 1 | 345 |  | 1793 |  |  | MI | 19 | [5 empty] | Planned | 3000000 | [8 empty] | Y | N | Y
937 | 2005-08-10 | BR | E-MIO | ITC | 908 | 2005-08-10 | ii | 2008-05-30 | Lulu | Lemoyne | 1 | 345 |  | 1536 |  |  | MI | 42 | [5 empty] | Planned | 3000000 | [8 empty] | Y | N | Y
934 | 2005-08-10 | BR | E-MIO | ITC | 908 | 2005-08-10 | ii | 2008-05-30 | Lulu | Majestic | 1 | 345 |  | 1195 |  |  | MI | 51 | [5 empty] | Planned | 3000000 | [8 empty] | Y | N | Y
935 | 2005-08-10 | BR | E-MIO | ITC | 908 | 2005-08-10 | ii | 2008-05-30 | Lulu | Milan | 1 | 345 |  | 2241 |  |  | MI | 16 | [5 empty] | Planned | 3000000 | [8 empty] | Y | N | Y
936 | 2005-08-10 | BR | E-MIO | ITC | 908 | 2005-08-10 | ii | 2008-05-30 | Lulu | Monroe 3-4 | 1 | 345 |  | 2008 |  |  | MI | 15 | [5 empty] | Planned | 3000000 | [8 empty] | Y | N | Y
1383 | 2005-08-10 | BR | E-MIO | ITC | 692 | 2005-08-10 | ITC8 | 2008-05-31 | Bismarck 345 kV | Troy 345 kV | 1 | 345 |  | 700 |  | N7 | MI |  | 15.4 | 100 |  |  |  | Planned | 45000000 | [8 empty] | Y | N | Y
1384 | 2005-08-10 | BR | E-MIO | ITC | 692 | 2005-08-10 | ITC8 | 2008-05-31 | Troy 345/120 kV | transformer | 1 | 345 | 120 | 700 |  | N7 | MI |  |  | 100 |  |  |  | Planned | 5000000 | [8 empty] | Y | N | Y
910 | 2006-07-05 | BR | E-MIO | ITC | 907 | 2005-08-10 | ITC17 | 2008-05-31 | Goodison 345 kV | Belle River 345 | 1 | 345 |  | 2151 |  | N7 | MI | 35.2 |  | 100 |  |  |  | Planned | 6000000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
913 | 2006-07-05 | BR | E-MIO | ITC | 907 | 2005-08-10 | ITC17 | 2008-05-31 | Goodison 120 kV | Pontiac 120 kV | 1 | 120 |  | 343 |  | N7 | MI |  | 6.3 | 100 |  |  |  | Planned | 11000000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
915 | 2006-07-05 | BR | E-MIO | ITC | 907 | 2005-08-10 | ITC17 | 2008-05-31 | Goodison 120 kV | Tienken 120 kV | 1 | 120 |  | 343 |  | N7 | MI | 2.78 | 2.34 | 100 |  |  |  | Planned | 5500000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
916 | 2006-07-05 | BR | E-MIO | ITC | 907 | 2005-08-10 | ITC17 | 2008-05-31 | Spokane 120 kV | Tienken 120 kV | 1 | 120 |  | 343 |  | N7 | MI | 0.1 |  | 100 |  |  |  | Planned | 5500000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
912 | 2006-07-05 | BR | E-MIO | ITC | 907 | 2005-08-10 | ITC17 | 2008-05-31 | Goodison 345/120 kV | transformer | 1 | 345 | 120 | 700 |  | N7 | MI |  |  | 100 |  |  |  | Planned | 5000000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
914 | 2006-07-05 | BR | E-MIO | ITC | 907 | 2005-08-10 | ITC17 | 2008-05-31 | Goodison 120 kV | Sunbird 120 kV | 1 | 120 |  | 229 |  | N7 | MI | 3.55 | 2.87 | 100 |  |  |  | Planned | 11000000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
911 | 2006-07-05 | BR | E-MIO | ITC | 907 | 2005-08-10 | ITC17 | 2008-05-31 | Goodison 345 kV | Pontiac 345 | 1 | 345 |  | 2002 |  | N7 | MI | 6.3 |  | 100 |  |  |  | Planned | 6000000 | [6 empty] | ITC - Jeff Wyman |  | Y | N | Y
1379 | 2005-11-28 | BR | E-MIO | ITC | 900 | 2005-08-10 | aa | 2008-12-31 | Coventry 120 kV | Duvall 120 kV | 1 | 120 |  | 200 |  | N7 | MI | 9.1 |  | 100 |  |  |  | Proposed | 750000 | [8 empty] | Y | N | Y
1380 | 2005-11-28 | BR | E-MIO | ITC | 900 | 2005-08-10 | aa | 2008-12-31 | Duvall 120 kV | Hager 120 kV | 1 | 120 |  | 347 |  | N7 | MI | 4.6 |  | 100 |  |  |  | Proposed | 750000 | [8 empty] | Y | N | Y
919 | 2006-07-05 | BR | E-MIO | ITC | 902 | 2005-08-10 | ITC12 | 2008-12-31 | Greenwood 345/120 kV | transformer | 2 | 345 | 120 | 700 |  | N6 | MI |  |  | 50 | 50 |  |  | Proposed | 5000000 |  |  |  |  | 2005-07-08 | MTEP06 | ITC - Jeff Wyman |  | Y | N | Y
920 | 2006-07-05 | BR | E-MIO | ITC | 902 | 2005-08-10 | ITC12 | 2008-12-31 | Greenwood 120 kV | Wabash 120 kV | 1 | 120 |  |  |  | N6 | MI | 10.9 | 11.8 | 100 |  |  |  | Proposed | 4000000 |  |  |  |  | 2005-07-08 | MTEP06 | ITC - Jeff Wyman |  | Y | N | Y
921 | 2006-07-05 | BR | E-MIO | ITC | 902 | 2005-08-10 | ITC12 | 2008-12-31 | Greenwood 120 kV | Adams 120 kV | 1 | 120 |  | 222 |  | N6 | MI | 15.7 | 12.7 | 100 |  |  |  | Proposed | 3000000 |  |  |  |  | 2005-07-08 | MTEP06 | ITC - Jeff Wyman |  | Y | N | Y
923 | 2006-07-05 | BR | E-MIO | ITC | 903 | 2005-08-10 | ITC13 | 2008-12-31 | Stephens 230/120 kV | Transformer | 1 | 230 | 120 | 693 |  | N7 | MI |  |  | 100 |  |  |  | Proposed | 4000000 |  |  |  |  | 2005-07-08 | MTEP06 | ITC - Jeff Wyman |  | Y | N | Y
924 | 2006-07-05 | BR | E-MIO | ITC | 903 | 2005-08-10 | ITC13 | 2008-12-31 | Stephens 120 kV | Redrun 120 kV | 1 | 120 |  | 343 |  | N7 | MI |  | 5.4 | 100 |  |  |  | Proposed | 2000000 |  |  |  |  | 2005-07-08 | MTEP06 | ITC - Jeff Wyman |  | Y | N | Y
922 | 2006-07-05 | BR | E-MIO | ITC | 903 | 2005-08-10 | ITC13 | 2008-12-31 | Bismark 230 kV | Stephens 230 | 1 | 230 |  | 657 |  | N7 | MI |  | 8.2 | 100 |  |  |  | Proposed | 3000000 | 131500000 |  |  |  | 2005-07-08 | MTEP06 | ITC - Jeff Wyman |  | Y | N | Y
1388 | 2005-01-14 | BR | E-MIO | ITC | 694 | 2005-06-15 | ITC9 | 2009-12-31 | Saratoga 120 kV | Bunce Creek 120 kV | 1 | 120 |  | 313 |  | N6 | MI | 12.5 | 0.6 | 100 |  |  |  | Proposed | 700000 |  |  |  |  | 2005-01-14 |  |  |  | Y | N | Y
1393 | 2005-01-14 | BR | E-MIO | ITC | 694 | 2005-06-15 | ITC9 | 2009-12-31 | Saratoga 345 kV | Belle River 345 | 1 | 345 |  | 2259 |  | N7 | MI | 16.5 | 4.2 | 100 |  |  |  | Proposed | 6000000 |  |  |  |  | 2005-01-14 |  |  |  | Y | N | Y
1386 | 2005-01-14 | BR | E-MIO | ITC | 694 | 2005-06-15 | ITC9 | 2009-12-31 | Saratoga 120 kV | Robin 120 kV | 1 | 120 |  | 444 |  | N6 | MI | 23.3 | 0.6 | 100 |  |  |  | Proposed | 700000 |  |  |  |  | 2005-01-14 |  |  |  | Y | N | Y
1385 | 2005-01-14 | BR | E-MIO | ITC | 694 | 2005-06-15 | ITC9 | 2009-12-31 | Saratoga 345/120 kV (sw sta provisions) | transformer |  | 345 | 120 |  |  | N6 | MI |  |  | 100 |  |  |  | Proposed | 1100000 |  |  |  | Build a new 345/120 kV switching station at Saratoga | 2005-01-14 |  |  |  | Y | N | Y
1392 | 2005-01-14 | BR | E-MIO | ITC | 694 | 2005-06-15 | ITC9 | 2009-12-31 | Saratoga 345 kV | Pontiac 345 kV | 1 | 345 |  | 1769 |  | N7 | MI | 42.9 |  | 100 |  |  |  | Proposed | 600000 |  |  |  |  | 2005-01-14 |  |  |  | Y | N | Y
1391 | 2005-01-14 | BR | E-MIO | ITC | 694 | 2005-06-15 | ITC9 | 2009-12-31 | Saratoga 345 kV | Greenwood 345 kV | 2 | 345 |  | 2552 |  | N6 | MI |  | 13.4 | 100 |  |  |  | Proposed | 13500000 |  |  |  |  | 2005-01-14 |  |  |  | Y | N | Y
1387 | 2005-01-14 | BR | E-MIO | ITC | 694 | 2005-06-15 | ITC9 | 2009-12-31 | Saratoga 120 kV | Wabash 120 kV | 1 | 120 |  | 299 |  | N6 | MI | 13.6 | 0.6 | 100 |  |  |  | Proposed | 700000 |  |  |  |  | 2005-01-14 |  |  |  | Y | N | Y
1390 | 2005-01-14 | BR | E-MIO | ITC | 694 | 2005-06-15 | ITC9 | 2009-12-31 | Saratoga 345 kV | Greenwood 345 kV | 1 | 345 |  | 2241 |  | N6 | MI | 13.4 |  | 100 |  |  |  | Proposed | 600000 |  |  |  |  | 2005-01-14 |  |  |  | Y | N | Y
1389 | 2005-01-14 | BR | E-MIO | ITC | 694 | 2005-06-15 | ITC9 | 2009-12-31 | Saratoga 120 kV | Burns 2 120 kV | 1 | 120 |  | 313 |  | N7 | MI | 17.7 | 0.6 | 100 |  |  |  | Proposed | 700000 |  |  |  |  | 2005-01-14 |  |  |  | Y | N | Y
1394 | 2005-01-14 | BR | E-MIO | ITC | 694 | 2005-06-15 | ITC9 | 2009-12-31 | Saratoga 345/120 kV | transformer | 1 | 345 | 120 | 700 |  | N6 | MI |  |  | 100 |  |  |  | Proposed | 5000000 | 29600000 |  |  |  | 2005-01-14 |  |  |  | Y | N | Y
944 | 2005-07-08 | BR | E-MIO | ITC | 909 | 2005-08-10 | jj | 2010-05-30 | Tuscola 230-120 kV | transformer | 1 | 230 | 120 | 557 |  |  | MI | [6 empty] | Proposed | 5000000 |  |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
943 | 2005-07-08 | BR | E-MIO | ITC | 909 | 2005-08-10 | jj | 2010-05-30 | Atlanta 230 | Tuscola 230 | 1 | 230 |  | 657 |  |  | MI |  | 13.6 |  |  |  |  | Proposed | 13500000 |  |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
942 | 2005-07-08 | BR | E-MIO | ITC | 909 | 2005-08-10 | jj | 2010-05-30 | Atlanta 345-230 kV | transformer | 1 | 345 | 230 | 665 |  |  | MI | [6 empty] | Proposed | 5000000 |  |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
945 | 2005-07-08 | BR | E-MIO | ITC | 909 | 2005-08-10 | jj | 2010-05-30 | Tuscola 230 | Hunters Creek 230 | 1 | 230 |  | 657 |  |  | MI |  | 22.5 |  |  |  |  | Proposed | 500000 |  |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
941 | 2005-07-08 | BR | E-MIO | ITC | 909 | 2005-08-10 | jj | 2010-05-30 | Atlanta Junct. | Atlanta 345 | 1 | 345 |  | 1553 |  |  | MI |  | 2.3 |  |  |  |  | Proposed | 3000000 |  |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
940 | 2005-07-08 | BR | E-MIO | ITC | 909 | 2005-08-10 | jj | 2010-05-30 | Atlanta Junct. | Thetford | 1 | 345 |  | 1554 |  |  | MI | 22 | [5 empty] | Proposed | 500000 |  |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
939 | 2005-07-08 | BR | E-MIO | ITC | 909 | 2005-08-10 | jj | 2010-05-30 | Atlanta Junct. | Hampton | 1 | 345 |  | 1554 |  |  | MI | 16 | [5 empty] | Proposed | 500000 |  |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
948 | 2005-07-08 | BR | E-MIO | ITC | 909 | 2005-08-10 | jj | 2010-05-30 | Hunters Creek 345-230 kV | transformer | 1 | 345 | 230 | 665 |  |  | MI | [6 empty] | Proposed | 5000000 |  |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
946 | 2005-07-08 | BR | E-MIO | ITC | 909 | 2005-08-10 | jj | 2010-05-30 | Hunters Creek 345 | Blackfoot 345 | 1 | 345 |  | 2002 |  |  | MI | 20 | [5 empty] | Proposed | 5000000 |  |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
947 | 2005-07-08 | BR | E-MIO | ITC | 909 | 2005-08-10 | jj | 2010-05-30 | Hunters Creek 345 | Belle River 345 | 1 | 345 |  | 2002 |  |  | MI | 45 | [5 empty] | Proposed | 5000000 |  |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
949 | 2005-07-08 | BR | E-MIO | ITC | 909 | 2005-08-10 | jj | 2010-05-30 | Hunters Creek 230-120 kV | transformer | 1 | 230 | 120 | 557 |  |  | MI | [6 empty] | Proposed | 5000000 | 48000000 |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
684 | 2004-12-23 | BR | N-Nebraska | LES | 590 | 2005-06-15 | TRN.440.05 | 2006-05-01 | 27th & Pine Lake | 40th & Rokeby | 1 | 115 |  | 373 | New Line | F9 | NE |  | 1 | 100 |  |  |  | Planned | 952500 | Planning |  | Y | [5 empty] | Y | Y | Y
685 | 2005-01-12 | BR | N-Nebraska | LES | 590 | 2005-06-15 | TRN.440.05 | 2006-05-01 | 56th & Pine Lake | 40th & Rokeby | 1 | 115 |  | 373 | New Line | F9 | NE |  | 1 | 100 |  |  |  | Planned | 952500 | Planning |  | Y | [5 empty] | Y | Y | Y
193 | 2005-07-13 | BR | N-Nebraska | LES | 246 | 2005-06-15 | TRN.410.02 | 2008-12-31 | NW68th & Holdrege | NW 12th & Arbor | 1 | 115 |  | 373 | New Line | F9 | NE |  | 10 | 100 |  |  |  | Planned | 1712000 | Planning |  | Y | Distribution interconnection. ISD adjustment to meet need |  | MTEP03 |  |  | Y | Y | Y
541 | 2005-08-31 | BR | N-Nebraska | LES | 247 | 2005-06-15 | TRN.610.06 | 2008-12-31 | Wagener | NW68th & Holdrege | 1 | 345 |  | 956 | New Line | F9 | NE |  | 26 | 100 |  |  |  | Planned | 28077000 | Planning |  | Y | Construction coordination with OPPD |  |  |  |  | Y | Y | Y
806 | 2005-07-08 | BR | N-Nebraska | LES | 804 | 2005-07-08 | TRN.440.07 | 2008-12-31 | 19th & Alvo | 70th & Bluff | 1 | 115 |  | 363 | Rebuilt Line | F9 | NE | 1.5 |  |  |  |  | 100 | Planned | 300000 | Planning |  | Y |  | 2005-07-08 | MTEP06 |  |  | Y | Y | Y
805 | 2005-07-08 | BR | N-Nebraska | LES | 805 | 2005-07-08 | TRN.601.03 | 2010-05-01 | NW68th & Holdrege 345/115 kV | transformer | 2 | 345 | 115 | 336 MVA | New Transformer | F9 | NE |  |  | 100 |  |  |  | Proposed | 3300000 | Planning |  | N |  | 2005-07-08 | MTEP06 |  |  | Y | Y | Y
1713 | 2005-11-18 | GEN | Central | LGEE | 1063 | 2005-11-18 |  | 2005-09-01 |  | generator |  |  |  | 95 | new generator |  | KY |  |  |  | 100 |  |  | Planned |  |  |  |  | not in model |  |  |  | G031 | Y | N | Y |  | Generator
1466 | 2005-07-08 | BR | E-IOK | LGEE | 937 | 2005-07-08 | 366 | 2005-11-30 | Blue Lick 345-161 | transformer | 1 | 345 | 161 | 240 | Upgrade | M11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Planned | 30000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1484 | 2005-07-08 | BR | E-IOK | LGEE | 952 | 2005-07-08 | 525 | 2005-11-30 | Arnold | Wooten Tap | 1 | 161 | 161 | 207 | Add | O11 | KY | 0 | 0 | 0 | 0 | 0 | 0 | Proposed | 1408000 | Planning MISO |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1485 | 2005-07-08 | BR | E-IOK | LGEE | 952 | 2005-07-08 | 525 | 2005-11-30 | Arnold | Delvinta | 1 | 161 |  | 0 | Remove | O11 | KY | 0 | 0 | 0 | 0 | 0 | 0 | Proposed |  | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1486 | 2005-07-08 | BR | E-IOK | LGEE | 952 | 2005-07-08 | 525 | 2005-11-30 | AEP Wooten | Wooten Tap | 1 | 161 |  | 167 | Add | O11 | KY | 0 | 0 | 0 | 0 | 0 | 0 | Proposed | 583000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1487 | 2005-07-08 | BR | E-IOK | LGEE | 952 | 2005-07-08 | 525 | 2005-11-30 | Delvinta | Wooten Tap | 1 | 161 |  | 161 | Add | O11 | KY | 0 | 0 | 0 | 0 | 0 | 0 | Proposed | 1408000 | Planning MISO |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1494 | 2005-07-08 | BR | E-IOK | LGEE | 959 | 2005-07-08 | 538 | 2005-11-30 | Delvinta | EKPC Beattyville Tap | 1 | 161 |  | 167 | Upgrade | O11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Proposed | 20000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
624 | 2005-07-08 | BR | E-IOK | LGEE | 935 | 2005-07-08 | 349 | 2006-03-30 | Blue Lick | Bullitt Co | 1 | 161 |  | 235 | Upgrade | M11 | KY | 6 | 0 | 100 | 0 | 0 | 0 | Planned | 300000 | Planning | [7 empty] | Y | N | Y
493 | 2005-11-28 | BR | E-IOK | LGEE | 313 | 2005-06-15 | LGEE3 | 2006-05-30 | Middletown | Buckner | 1 | 345 |  | 1066 |  |  | KY | 0 |  | 100 |  |  |  | Planned | 5000 |  |  |  | Planned for the spring |  |  |  |  | Y | N | Y
485 | 2005-07-08 | BR | E-IOK | LGEE | 936 | 2005-07-08 | 360 | 2006-05-30 | Fawkes | Fawkes Tap | 1 | 138 |  | 200 | Upgrade | N11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Proposed | 75000 | Planning | [7 empty] | Y | N | Y
1489 | 2005-07-08 | BR | E-IOK | LGEE | 954 | 2005-07-08 | 528 | 2006-05-30 | Middletown | Buckner | 1 | 345 |  | 1195 | Upgrade | M11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Proposed | 3000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1490 | 2005-07-08 | BR | E-IOK | LGEE | 955 | 2005-07-08 | 529 | 2006-05-30 | Middletown | Trimble Co | 1 | 345 |  | 1195 | Upgrade | M10 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Proposed | 3000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1491 | 2005-07-08 | BR | E-IOK | LGEE | 956 | 2005-07-08 | 531 | 2006-05-30 | Green River | Ohio Co | 2 | 138 |  | 169 | Upgrade | M11 | KY | 14 | 0 | 100 | 0 | 0 | 0 | Proposed | 300000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1497 | 2005-07-08 | BR | E-IOK | LGEE | 962 | 2005-07-08 | 1002 | 2006-05-30 | Paris 138-69 | transformer | 1 | 138 | 69 | 150 | Add | N11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Planned | 1200000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1498 | 2005-07-08 | BR | E-IOK | LGEE | 962 | 2005-07-08 | 1002 | 2006-05-30 | Paris | EKPC Paris Tap | 1 | 138 |  | 179 | Add | N11 | KY | 0 | 6 | 100 | 0 | 0 | 0 | Planned | 2200000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1500 | 2005-07-08 | BR | E-IOK | LGEE | 963 | 2005-07-08 | 1004 | 2006-08-30 | Virginia City 138-69 | transformer | 1 | 138 | 69 | 120 | Add | O11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Planned | 1400000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1499 | 2005-07-08 | BR | E-IOK | LGEE | 963 | 2005-07-08 | 1004 | 2006-08-30 | Virginia City | AEP Clinch River | 1 | 138 |  | 177 | Add | O11 | KY | 0 | 8 | 100 | 0 | 0 | 0 | Planned | 3500000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1469 | 2005-07-08 | BR | E-IOK | LGEE | 940 | 2005-07-08 | 394 | 2006-11-30 | EKPC Goddard | Goddard | 1 | 138 |  | 0 | Remove | N10 | KY | 0 | 0 | 0 | 0 | 0 | 0 | Proposed | 0 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1472 | 2005-07-08 | BR | E-IOK | LGEE | 941 | 2005-07-08 | 395 | 2006-11-30 | Kenton | Wedonia | 1 | 138 |  | 143 | Add | N10 | KY | 0 | 0 | 0 | 0 | 0 | 0 | Proposed | 0 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1471 | 2005-07-08 | BR | E-IOK | LGEE | 941 | 2005-07-08 | 395 | 2006-11-30 | Wedonia | Kenton Reactor | 1 | 138 | 138 | 0 | Remove | N10 | KY | 0 | 0 | 0 | 0 | 0 | 0 | Proposed | 0 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1470 | 2005-07-08 | BR | E-IOK | LGEE | 941 | 2005-07-08 | 395 | 2006-11-30 | Kenton | Kenton Reactor | 1 | 138 | 138 | 0 | Remove | N10 | KY | 0 | 0 | 0 | 0 | 0 | 0 | Proposed | 0 | Planning | 8686000 |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1772 | 2005-11-18 | GEN | Central | LGEE | 1122 | 2005-11-18 |  | 2007-01-01 |  | generator | 2 |  |  | 750 | new generator |  | KY |  |  |  | 100 |  |  | Planned |  |  |  |  | 27499 |  |  |  | G218 | Y | N | Y |  | Generator
1923 | 2006-02-27 | BR | E-IOK | LGEE | 1224 | 2006-02-27 | 1024 | 2007-03-31 | NAS 345-138 | transformer | 1 | 345 | 138 | 450 | Add new transformer |  | KY |  |  | 100 |  |  |  | Planned |  |  |  |  | Need cost estimate | 2006-02-27 |  |  | NAS 2/1/06 - M Toll | Y | N | Y
1922 | 2006-02-27 | BR | E-IOK | LGEE | 1224 | 2006-02-27 | 1024 | 2007-03-31 | NAS | NAS tap | 1 | 138 |  | 221 | Add |  | KY |  |  | 100 |  |  |  | Planned | [5 empty] | 2006-02-27 |  |  | NAS 2/1/06 - M Toll | Y | N | Y
1920 | 2006-02-27 | BR | E-IOK | LGEE | 1224 | 2006-02-27 | 1024 | 2007-03-31 | Dayton Walther Tap | NAS tap | 1 | 138 |  | 221 | Add |  | KY |  |  | 100 |  |  |  | Planned | [5 empty] | 2006-02-27 |  |  | NAS 2/1/06 - M Toll | Y | N | Y
1919 | 2006-02-27 | BR | E-IOK | LGEE | 1224 | 2006-02-27 | 1024 | 2007-03-31 | Ghent | NAS | 1 | 138 |  | 0 | Remove |  | KY |  |  | 100 |  |  |  | Planned | [5 empty] | 2006-02-27 |  |  | NAS 2/1/06 - M Toll | Y | N | Y
1921 | 2006-02-27 | BR | E-IOK | LGEE | 1224 | 2006-02-27 | 1024 | 2007-03-31 | Dayton Walther Tap | NAS | 1 | 138 |  | 0 | Remove |  | KY |  |  | 100 |  |  |  | Planned | [5 empty] | 2006-02-27 |  |  | NAS 2/1/06 - M Toll | Y | N | Y
1918 | 2006-02-27 | BR | E-IOK | LGEE | 1224 | 2006-02-27 | 1024 | 2007-03-31 | Ghent | NAS tap | 1 | 138 |  | 221 | Add |  | KY |  |  | 100 |  |  |  | Planned | [5 empty] | 2006-02-27 |  |  | NAS 2/1/06 - M Toll | Y | N | Y
484 | 2005-07-08 | BR | E-IOK | LGEE | 317 | 2005-07-08 | 364 | 2007-05-30 | Mill Creek | Manslick | 1 | 138 |  | 192 | Upgrade | M11 | KY | 10 | 0 | 100 | 0 | 0 | 0 | Proposed | 83000 | Planning | [7 empty] | Y | N | Y
1463 | 2005-07-08 | BR | E-IOK | LGEE | 932 | 2005-07-08 | 180 | 2007-05-30 | Hardin Co 345-138 | transformer | 2 | 345 | 138 | 450 | Add | M11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Proposed | 5010000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1924 | 2006-02-27 | BR | E-IOK | LGEE | 1223 | 2006-02-27 | 111 | 2007-05-30 | Dayton Walther Tap | NAS | 1 | 138 |  | 221 | Upgrade |  | KY |  |  | 100 |  |  |  | Planned |  |  |  |  | Need cost estimate | 2006-02-27 |  |  | NAS 2/1/06 - M Toll | Y | N | Y
629 | 2005-07-08 | BR | E-IOK | LGEE | 309 | 2005-07-08 | 487 | 2007-11-30 | Lake Reba Tap | West Irvine Tap | 1 | 161 |  | 167 | Upgrade | N11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Proposed | 20000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1474 | 2005-07-08 | BR | E-IOK | LGEE | 944 | 2005-07-08 | 484 | 2007-11-30 | Fawkes | Fawkes Tap | 1 | 138 |  | 200 | Upgrade | N11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Proposed | 20000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1476 | 2005-07-08 | BR | E-IOK | LGEE | 946 | 2005-07-08 | 486 | 2007-11-30 | Fawkes | EKPC Fawkes | 1 | 138 |  | 257 | Upgrade | N11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Proposed | 30000 | Planning | 5163000 |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1492 | 2005-07-08 | BR | E-IOK | LGEE | 957 | 2005-07-08 | 534 | 2008-05-30 | Paddys Run | Paddys West | 1 | 138 |  | 305 | Upgrade | M11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Proposed | 3000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1503 | 2005-07-08 | BR | E-IOK | LGEE | 964 | 2005-07-08 | 1005 | 2008-05-30 | Middletown | Ford | 1 | 69 |  | 123 | Remove | M11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Proposed | 0 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1501 | 2005-07-08 | BR | E-IOK | LGEE | 964 | 2005-07-08 | 1005 | 2008-05-30 | Middletown | Ford | 1 | 138 |  | 247 | Add | M11 | KY | 6 | 0 | 100 | 0 | 0 | 0 | Proposed | 551000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1502 | 2005-07-08 | BR | E-IOK | LGEE | 964 | 2005-07-08 | 1005 | 2008-05-30 | Ford 138-69 kV | transformer | 1 | 138 | 69 | 150 | Add | M11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Proposed | 992000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1714 | 2005-11-18 | GEN | Central | LGEE | 1064 | 2005-11-18 |  | 2008-06-01 |  | generator |  |  |  | 95 | new generator |  | KY |  |  |  | 100 |  |  | Planned |  |  |  |  | not in model |  |  |  | G032 | Y | N | Y |  | Generator
1504 | 2005-07-08 | BR | E-IOK | LGEE | 965 | 2005-07-08 | 1006 | 2008-09-30 | Lake Reba Tap | West Irvine Tap | 1 | 161 |  | 0 | Remove | N11 | KY | 0 | 0 | 0 | 100 | 0 | 0 | Planned | 0 | Planning |  |  |  | 2005-07-08 | MTEP06 |  | G243 | Y | N | Y |  | Network
1505 | 2005-07-08 | BR | E-IOK | LGEE | 965 | 2005-07-08 | 1006 | 2008-09-30 | West Irvine 161-69 kV | transformer | 1 | 161 | 69 | 90 | Upgrade | N11 | KY | 0 | 0 | 0 | 0 | 100 | 0 | Planned | 620000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  | G243 | Y | N | Y |  | Network | Y
1506 | 2005-07-08 | BR | E-IOK | LGEE | 965 | 2005-07-08 | 1006 | 2008-09-30 | West Irvine | West Irvine Tap | 1 | 161 |  | 0 | Remove | N11 | KY | 0 | 0 | 0 | 100 | 0 | 0 | Planned | 0 | Planning |  |  |  | 2005-07-08 | MTEP06 |  | G243 | Y | N | Y |  | Network
1507 | 2005-07-08 | BR | E-IOK | LGEE | 965 | 2005-07-08 | 1006 | 2008-09-30 | West Irvine | Lake Reba Tap | 1 | 161 |  | 167 | Add | N11 | KY | 0 | 0 | 0 | 100 | 0 | 0 | Planned | 0 | Planning |  |  |  | 2005-07-08 | MTEP06 |  | G243 | Y | N | Y |  | Network
1508 | 2005-07-08 | BR | E-IOK | LGEE | 965 | 2005-07-08 | 1006 | 2008-09-30 | Delvinta | West Irvine Tap | 1 | 161 |  | 0 | Remove | N11 | KY | 0 | 0 | 0 | 100 | 0 | 0 | Planned | 0 | Planning |  |  |  | 2005-07-08 | MTEP06 |  | G243 | Y | N | Y |  | Network
1509 | 2005-07-08 | BR | E-IOK | LGEE | 965 | 2005-07-08 | 1006 | 2008-09-30 | West Irvine | Delvinta | 1 | 161 |  | 176 | Add | N11 | KY | 0 | 3 | 0 | 100 | 0 | 0 | Planned | 1200000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  | G243 | Y | N | Y |  | Network
1475 | 2005-07-08 | BR | E-IOK | LGEE | 945 | 2005-07-08 | 485 | 2008-11-30 | Fawkes | Fawkes Tap | 1 | 138 |  | 218 | Upgrade | N11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Proposed | 20000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1783 | 2005-11-18 | GEN | Central | LGEE | 1133 | 2005-11-18 |  | 2008-12-15 | Estill Co E.P. | generator |  |  |  | 120 | new generator |  | KY |  |  |  | 100 |  |  | Planned |  |  | 3386000 | [5 empty] | G243 | Y | N | Y |  | Generator
1459 | 2005-07-08 | BR | E-IOK | LGEE | 928 | 2005-07-08 | 50 | 2009-05-30 | Brown North | Pisgah | 1 | 138 |  | 222 | Upgrade | N11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Proposed | 20000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1460 | 2005-07-08 | BR | E-IOK | LGEE | 929 | 2005-07-08 | 64 | 2009-05-30 | Brown North | Higby Mill | 1 | 138 |  | 222 | Upgrade | N11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Proposed | 20000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1480 | 2005-07-08 | BR | E-IOK | LGEE | 948 | 2005-07-08 | 520 | 2009-05-30 | Brown CT | Bardstown | 1 | 138 |  | 191 | Upgrade | N11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Proposed | 3000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1482 | 2005-07-08 | BR | E-IOK | LGEE | 950 | 2005-07-08 | 523 | 2009-05-30 | Fawkes Tap | Lake Reba Tap | 1 | 138 |  | 177 | Upgrade | N11 | KY | 5 | 0 | 100 | 0 | 0 | 0 | Proposed | 300000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1488 | 2005-07-08 | BR | E-IOK | LGEE | 953 | 2005-07-08 | 527 | 2009-05-30 | Lebanon | Mercer Co | 1 | 138 |  | 177 | Upgrade | N11 | KY | 9 | 0 | 100 | 0 | 0 | 0 | Proposed | 300000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1493 | 2005-07-08 | BR | E-IOK | LGEE | 958 | 2005-07-08 | 535 | 2009-05-30 | Paddys Run | Paddys West | 1 | 138 |  | 359 | Upgrade | M11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Proposed | 20000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
161 | 2006-04-10 | BR | E-IOK | LGEE | 314 | 2005-07-08 | 543 | 2009-11-30 | Lake Reba Tap | EKPC Union City | 1 | 138 |  | 251 | Upgrade | N11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Proposed | 10000 | Planning |  |  | Reduced load forecast |  |  | Mike Toll |  | Y | N | Y
1461 | 2005-07-08 | BR | E-IOK | LGEE | 930 | 2005-07-08 | 72 | 2009-11-30 | Loudon Ave | EKPC Avon Reactor | 1 | 138 | 138 | 222 | Upgrade | N11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Proposed | 160000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1495 | 2005-07-08 | BR | E-IOK | LGEE | 960 | 2005-07-08 | 539 | 2009-11-30 | Carrollton | Lockport | 1 | 138 |  | 182 | Upgrade | N10 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Proposed | 50000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
139 | 2005-07-08 | BR | E-IOK | LGEE | 943 | 2005-07-08 | 402 | 2009-12-30 | Ghent | Owen Co Tap | 1 | 138 |  | 243 | Upgrade | N10 | KY | 12 | 0 | 100 | 0 | 0 | 0 | Planned | 240000 | Planning |  |  |  | 2005-07-08 | mtep |  | A024, A091, A099 | Y | N | Y |  |  | Y
157 | 2005-07-08 | BR | E-IOK | LGEE | 966 | 2005-07-08 | 1007 | 2009-12-30 | Mill Creek | Hardin Co | 1 | 345 |  | 1195 | Add | M11 | KY | 0 | 42 | 100 | 0 | 0 | 0 | Planned | 56570000 | Planning | [6 empty] | A024, A091, A099 | Y | N | Y |  |  | Y
1510 | 2005-07-08 | BR | E-IOK | LGEE | 967 | 2005-07-08 | 1008 | 2009-12-30 | Higby Mill | West Lexington | 1 | 138 |  | 177 | Add | N11 | KY | 0 | 12 | 100 | 0 | 0 | 0 | Planned | 3203000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  | A024, A091, A099 | Y | N | Y |  |  | Y
1511 | 2005-07-08 | BR | E-IOK | LGEE | 968 | 2005-07-08 | 1009 | 2009-12-30 | West Frankfort | Tyrone | 1 | 138 |  | 222 | Add | N11 | KY | 0 | 10 | 100 | 0 | 0 | 0 | Planned | 4000000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  | A024, A091, A099 | Y | N | Y |  |  | Y
1514 | 2005-07-08 | BR | E-IOK | LGEE | 970 | 2005-07-08 | 1016 | 2009-12-30 | Elizabethtown | Hardin Co | 1 | 138 |  | 243 | Upgrade | M11 | KY | 1 | 0 | 0 | 100 | 0 | 0 | Planned | 40000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  | A024, A091, A099 | Y | N | Y |  |  | Y
1457 | 2005-07-08 | BR | E-IOK | LGEE | 25 | 2005-07-08 | 1010 | 2009-12-31 | CIN Trimble Co | Trimble Co | 1 | 345 |  | 1195 | Add | M10 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Planned | 0 | Planning |  |  |  | 2005-07-08 | MTEP06 |  | A024, A091, A099 | Y | N | Y |  |  | Y
593 | 2005-08-18 | BR | E-IOK | LGEE | 25 | 2005-07-08 | 1010 | 2009-12-31 | Elizabethtown | Hardin County | 1 | 138 |  | 224 |  | M11 | KY |  | 1.3 | 50 |  | 50 |  | Planned | 1106000 | [7 empty] | A024, A091, A099 | Y | N | Y |  |  | Y
160 | 2005-07-08 | BR | E-IOK | LGEE | 25 | 2005-07-08 | 1010 | 2009-12-31 | CIN Speed | Trimble Co | 1 | 345 |  | 1195 | Add | M10 | KY | 0 | 3 | 100 | 0 | 0 | 0 | Planned | 0 | Planning | [6 empty] | G218, A024, A091, A099 | Y | N | Y |  | Network | Y
1456 | 2005-07-08 | BR | E-IOK | LGEE | 25 | 2005-07-08 | 1010 | 2009-12-31 | Ghent | CIN Speed | 1 | 345 |  | 0 | Remove because of Trimble tap | M10 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Planned | 0 | Planning |  |  |  | 2005-07-08 | MTEP06 |  | A024, A091, A099 | Y | N | Y |  |  | Y
159 | 2005-07-08 | BR | E-IOK | LGEE | 25 | 2005-07-08 | 1010 | 2009-12-31 | Ghent | CIN Trimble Co | 1 | 345 |  | 1195 | Add | M10 | KY | 0 | 3 | 100 | 0 | 0 | 0 | Planned | 13179000 | Planning | [6 empty] | G218, A024, A091, A099 | Y | N | Y |  | Network | Y
626 | 2005-08-18 | BR | E-IOK | LGEE | 967 | 2005-07-08 | 1008 | 2009-12-31 | West Lexington | Higby Mill | 1 | 138 |  | 179 |  |  | KY |  | 11.8 | 50 |  | 50 |  | Planned | 2864000 | [8 empty] | Y | N | Y
625 | 2005-08-18 | BR | E-IOK | LGEE | 968 | 2005-07-08 | 1009 | 2009-12-31 | West Frankfort | Tyrone | 1 | 138 |  | 224 |  |  | KY |  | 10.2 | 50 | 50 |  |  | Planned | 9003000 |  | 91088000 | [6 empty] | Y | N | Y
1464 | 2005-07-08 | BR | E-IOK | LGEE | 933 | 2005-07-08 | 182 | 2010-05-30 | Hardin Co 345-138 kv | transformer | 1 | 345 | 138 | 448 | Upgrade | M11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Proposed | 57000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1465 | 2005-07-08 | BR | E-IOK | LGEE | 934 | 2005-07-08 | 332 | 2010-05-30 | Brown North | Tyrone | 1 | 138 |  | 177 | Upgrade | N11 | KY | 20 | 0 | 100 | 0 | 0 | 0 | Proposed | 300000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1467 | 2005-07-08 | BR | E-IOK | LGEE | 938 | 2005-07-08 | 367 | 2010-05-30 | Middletown 345-138 | transformer | 4 | 345 | 138 | 450 | Add | M11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Proposed | 5523000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1468 | 2005-07-08 | BR | E-IOK | LGEE | 939 | 2005-07-08 | 375 | 2010-05-30 | Northside | Jeffersonville Tap | 1 | 138 |  | 371 | Upgrade | M10 | IN | 2 | 0 | 100 | 0 | 0 | 0 | Proposed | 50000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1483 | 2005-07-08 | BR | E-IOK | LGEE | 951 | 2005-07-08 | 524 | 2010-05-30 | Hardin Co | Hardinsburg | 1 | 138 |  | 222 | Upgrade | M11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Proposed | 20000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1496 | 2005-07-08 | BR | E-IOK | LGEE | 961 | 2005-07-08 | 544 | 2010-05-30 | Algonquin | Dixie | 1 | 138 |  | 191 | Upgrade | M11 | KY | 0 | 0 | 100 | 0 | 0 | 0 | Proposed | 3000 | Planning | 5953000 |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1513 | 2005-07-08 | BR | E-IOK | LGEE | 969 | 2005-07-08 | 1012 | 2011-05-30 | Kosmos Cement | Tip Top | 1 | 138 |  | 222 | Add | M11 | KY | 0 | 14 | 100 | 0 | 0 | 0 | Proposed | 1000000 | Planning |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1512 | 2005-07-08 | BR | E-IOK | LGEE | 969 | 2005-07-08 | 1012 | 2011-05-30 | Mill Creek | Kosmos Cement | 1 | 138 |  | 143 | Upgrade | M11 | KY | 1 | 0 | 100 | 0 | 0 | 0 | Proposed | 33000 | Planning | 1033000 |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1869 | 2005-12-05 | BR | Central | LGEE |  |  |  |  | Shelby County | Shelby County tap |  | 69 |  |  | Open the 69kV tie from Shelby County (EKPC) to Shelby County Tap (LGEE) | [6 empty] | 100 |  | Planned |  |  |  |  | Submitted by MISO |  |  |  | A024, A091, A099 | Y | N | Y |  |  | Y
1784 | 2005-11-18 | GEN | West | MDU | 1134 | 2005-11-18 |  | 2003-12-01 | Dakota I PP | generator |  |  |  | 19 | new generator |  | ND |  |  |  | 100 |  |  | Under Construction | [8 empty] | G248 | Y | N | Y |  | Generator
1836 | 2005-11-18 | GEN | West | MDU | 1186 | 2005-11-18 |  | 2004-03-01 | GLENDCT | generator |  |  |  | 2 | new generator |  | MT |  |  |  | 100 |  |  | Under Construction | [8 empty] | G409 | Y | N | Y |  | Generator
1576 | 2005-08-02 | BR | N-NM | MDU | 548 | 2005-08-02 |  | 2007-11-01 | Bismarck Downtown | East Bismarck |  | 115 |  | 160 | Rebuild | D4 | ND |  |  | 100 |  |  |  | Planned | 363000 | Planning MISO | [7 empty] | Y | Y | Y
1578 | 2005-08-02 | BR | N-NM | MDU | 1008 | 2005-08-02 |  | 2009-11-01 | S Mandan | Bismarck Downtown |  | 115 |  | 180 | Memorial Bridge circuit replacement | D4 | ND |  |  | 100 |  |  |  | Planned | 2868000 | Planning MISO |  |  |  | 2005-08-02 | MTEP06 |  |  | Y | Y | Y
1577 | 2005-08-02 | BR | N-NM | MDU | 1008 | 2005-08-02 |  | 2009-11-01 | Heskett | NW Bismarck |  | 115 |  | 180 | Memorial Bridge circuit replacement | D4 | ND |  |  | 100 |  |  |  | Planned | 3692000 | Planning MISO | 6560000 |  |  | 2005-08-02 | MTEP06 |  |  | Y | Y | Y
1764 | 2005-11-18 | GEN | East | MECS | 1114 | 2005-11-18 |  | 2006-07-01 |  | generator |  |  |  | 630 | new generator |  | MI |  |  |  | 100 |  |  | Planned | [8 empty] | G217 CONS 111 | Y | N | Y |  | Generator
3081 | 2006-07-05 | DV | East | METC | 773 | 2005-07-27 | 47 | 2005-12-31 | Tittabawassee & Kenowa | Breaker Replacements |  | 345 |  | 3000 Amp | breaker replacement | N6 & M7 | MI | 0 |  | 100 |  |  |  | Planned | 1600000 |  |  |  | Construction Delays |  |  | METC - Russ Vente |  | Y | N | Y
1540 | 2006-07-05 | BR | East | METC | 977 | 2005-07-27 | 49 | 2006-05-01 | Marquette Station | Replace breaker failure scheme |  | 138 |  |  | Replace breaker failure scheme |  | MI | [6 empty] | Proposed | 200000 |  |  |  |  | 2005-07-27 | MTEP06 | METC - Russ Vente |  | Y | N | Y
1326 | 2006-07-05 | BR | East | METC | 643 | 2005-07-27 | 60 | 2006-06-01 | Gaines | Thompson Road | 1 | 138 |  |  |  | M7 | MI | 15 |  | 100 |  |  |  | Under Construction | 1425000 | [6 empty] | METC - Russ Vente |  | Y | N | Y
3082 | 2006-07-05 | DV | East | METC | 774 | 2005-07-27 | 61 | 2006-06-01 | Gaylord | Capacitors | 1 | 138 |  | 36 Mvar |  | M6 | MI | 0 |  | 100 |  |  |  | Under Construction | 900000 | [6 empty] | METC - Russ Vente |  | Y | N | Y | METC_2011Sum_U2_8-12-2005_29.idv
3083 | 2006-07-05 | DV | East | METC | 775 | 2005-07-27 | 62 | 2006-06-01 | Iosco | Capacitors | 1 | 138 |  | 18 Mvar |  | N6 | MI | 0 |  | 100 |  |  |  | Under Construction | 800000 | [6 empty] | METC - Russ Vente |  | Y | N | Y | METC_2011Sum_U2_8-12-2005_29.idv
1543 | 2006-07-05 | BR | East | METC | 980 | 2005-07-27 | 59 | 2006-06-01 | Arthur J. - Cobb - Tallmadge #1 | Arthur | 1 | 138 |  |  | Install aTap Pole and one two-way switch |  | MI | [6 empty] | Under Construction | 160000 |  |  |  |  | 2005-07-27 | MTEP06 | METC - Russ Vente |  | Y | N | Y
1586 | 2006-07-05 | DV | East | METC | 1014 | 2005-08-12 | 130 | 2006-06-01 | Oakland | Oakland - Capacitor Increase | 1 | 138 |  | 50.4 Mvar | Oakland - Increase Capacitor Size from 36 MVAR to 50.4 MVAR |  | MI |  |  | 100 |  |  |  | Under Construction | 75000 |  |  |  |  | 2005-08-12 | MTEP06 | METC - Russ Vente |  | Y | N | Y | METC_2011Sum_U2_8-12-2005_29.idv
1317 | 2006-03-16 | BR | E-MIO | METC | 494 | 2005-07-27 | 58 | 2006-12-01 | Battle Creek | Verona(Sag) | 2 | 138 |  |  |  | M7 | MI | 1 |  | 100 |  |  |  | Proposed | 50000 |  |  |  | Construction Issues |  |  | METC - Russ Vente |  | Y | N | Y
3080 | 2006-07-05 | DV | East | METC | 772 | 2006-07-05 | 66 | 2006-12-01 | Tallmadge | Transformer Bushing Replacements | 2 | 345 | 138 | TBD | The Spare Transformer is used as the 2nd Bank | M7 | MI | 0 |  | 100 |  |  |  | Under Construction | 258000 |  |  |  | Low system need (enable delay) Material delays |  |  | METC - Russ Vente |  | Y | N | Y | METC_2011Sum_U2_8-12-2005_29.idv
1438 | 2005-07-27 | BR | E-MIO | METC | 741 | 2005-07-27 | 71 | 2006-12-31 | Battle Creek | Oneida | 1 | 345 |  |  | relaying & communications | M7 | MI | 0 |  |  |  |  | 100 | Proposed | 3000000 | [8 empty] | Y | N | Y
1439 | 2005-07-27 | BR | E-MIO | METC | 741 | 2005-07-27 | 70 | 2006-12-31 | Argenta | Tompkins | 1 | 345 |  |  | relaying & communications | M7 | MI | 0 |  |  |  |  | 100 | Proposed | 2415000 | [8 empty] | Y | N | Y
1437 | 2005-07-27 | BR | E-MIO | METC | 741 | 2005-07-27 | 69 | 2006-12-31 | Argenta | Battle Creek | 1 | 345 |  |  | relaying & communications | M7 | MI | 0 |  |  |  |  | 100 | Proposed | 3000000 |  | 13883000 | [6 empty] | Y | N | Y
1436 | 2006-07-05 | BR | East | METC | 740 | 2006-07-05 | 46 | 2007-03-01 | Livingston | Gallagher | 1 | 345 |  |  | relaying & communications | M5 | MI | 0 |  |  |  |  | 100 | Planned | 794000 |  |  |  | Construction Delays |  |  | METC - Russ Vente |  | Y | N | Y
1434 | 2006-07-05 | BR | East | METC | 740 | 2006-07-05 | 44 | 2007-03-01 | Gallagher | Tittabawassee | 1 | 345 |  |  | relaying & communications | M5 | MI | 0 |  |  |  |  | 100 | Planned | 1000000 |  |  |  | Construction Delays |  |  | METC - Russ Vente |  | Y | N | Y
1435 | 2006-07-05 | BR | East | METC | 740 | 2006-07-05 | 45 | 2007-03-01 | Keystone | Livingston | 1 | 345 |  |  | relaying & communications | M5 | MI | 0 |  |  |  |  | 100 | Planned | 1000000 |  |  |  | Construction Delays |  |  | METC - Russ Vente |  | Y | N | Y
1332 | 2005-07-29 | BR | E-MIO | METC | 481 | 2005-07-27 | 74 | 2007-05-01 | Tallmadge 3rd 345/138 kV | transformer | 3 | 345 | 138 |  |  | M7 | MI | 0 |  | 100 |  |  |  | Proposed | 13500000 | [8 empty] | Y | N | Y
1534 | 2005-07-27 | BR | E-MIO | METC | 493 | 2005-07-27 | 123 | 2007-05-01 | Tallmadge Remove Reactors | Tallmadge Remove Reactors | 1&2 | 345 |  |  |  |  | MI | [6 empty] | Proposed | 20000 | Planning MISO |  |  |  | 2005-07-27 | MTEP06 |  |  | Y | N | Y
1327 | 2005-11-28 | BR | E-MIO | METC | 644 | 2005-07-27 | 64 | 2007-06-01 | Rogue River J. - METC | Rogue River | 1 | 138 |  |  |  | M7 | MI |  | 0.1 | 100 |  |  |  | Planned | 160000 |  |  |  | Customer requirement changed |  |  |  |  | Y | N | Y
1328 | 2006-03-16 | BR | E-MIO | METC | 645 | 2005-07-27 | 56 | 2007-06-01 | American Bumper | David | 1 | 138 |  |  |  | M7 | MI | 8 |  | 100 |  |  |  | Proposed | 2500000 |  |  |  | Construction Delays |  |  | METC - Russ Vente |  | Y | N | Y
1333 | 2005-07-27 | BR | E-MIO | METC | 648 | 2005-07-27 | 75 | 2007-06-01 | METC | Various Distribution Connections | 1 | 138 |  |  |  | Various | MI |  | 1 | 100 |  |  |  | Proposed | 2000000 | [8 empty] | Y | N | Y
3084 | 2005-07-27 | DV | E-MIO | METC | 776 | 2005-07-27 | 76 | 2007-06-01 | Various | Capacitors |  | 138 |  | 72 Mvar |  | various | MI | 0 |  | 100 |  |  |  | Proposed | 2000000 | [8 empty] | Y | N | Y
1539 | 2006-07-05 | BR | East | METC | 976 | 2005-07-27 | 48 | 2007-06-01 | Alpine | Add one line switch |  | 138 |  |  | Add One switch |  | MI | [6 empty] | Planned | 80000 |  |  |  | Delayed, Reduced load forecast | 2005-07-27 | MTEP06 | METC - Russ Vente |  | Y | N | Y
1545 | 2006-07-05 | BR | East | METC | 982 | 2005-07-27 | 65 | 2007-06-01 | Crahen J. -Spaudling - Race Street | Crahen | 1 | 138 |  |  | Install a Tap Pole and one switch |  | MI | [6 empty] | Planned | 80000 |  |  |  | Delayed due to load forecast reduction | 2005-07-27 | MTEP06 | METC - Russ Vente |  | Y | N | Y
1588 | 2005-08-12 | DV | E-MIO | METC | 1016 | 2005-08-12 | 132 | 2007-06-01 | Bard Road | Bard Road - New Capacitor | 1 | 138 |  | 36 Mvar | Bard Road - New 36 Mvar Capacitor |  | MI |  |  | 100 |  |  |  | Proposed | 596000 | Planning MISO |  |  |  | 2005-08-12 | MTEP06 |  |  | Y | N | Y
1589 | 2005-08-12 | DV | E-MIO | METC | 1017 | 2005-08-12 | 133 | 2007-06-01 | Croton | Croton - New Capacitor | 1 | 138 |  | 36 Mvar | Croton - New 36 Mvar Capacitor |  | MI |  |  | 100 |  |  |  | Proposed | 596000 | Planning MISO |  |  |  | 2005-08-12 | MTEP06 |  |  | Y | N | Y
1440 | 2005-07-27 | BR | E-MIO | METC | 742 | 2005-07-27 | 79 | 2007-12-31 | Nelson Road | Kenowa | 1 | 345 |  |  | relaying & communications | M7 | MI | 0 |  |  |  |  | 100 | Proposed | 2000000 | [8 empty] | Y | N | Y
1441 | 2005-07-27 | BR | E-MIO | METC | 742 | 2005-07-27 | 80 | 2007-12-31 | Nelson Road | Goss | 1 | 345 |  |  | relaying & communications | M7 | MI | 0 |  |  |  |  | 100 | Proposed | 2000000 | [8 empty] | Y | N | Y
1442 | 2005-07-27 | BR | E-MIO | METC | 742 | 2005-07-27 | 78 | 2007-12-31 | Goss | Thetford | 1 | 345 |  |  | relaying & communications | M7 | MI | 0 |  |  |  |  | 100 | Proposed | 1730000 |  | 30056000 | [6 empty] | Y | N | Y
1329 | 2006-03-16 | BR | E-MIO | METC | 646 | 2005-07-27 | 86 | 2008-06-01 | Edenville J. | Warren | 1 | 138 |  |  |  | M6 | MI | 14.8 |  | 100 |  |  |  | Proposed | 4000000 |  |  |  | System Need Changed |  |  | METC - Russ Vente |  | Y | N | Y
1339 | 2005-07-27 | BR | E-MIO | METC | 653 | 2005-07-27 | 88 | 2008-06-01 | METC | Various Distribution Connections | 1 | 138 |  |  |  | Various | MI |  | 1 | 100 |  |  |  | Proposed | 2000000 | [8 empty] | Y | N | Y
3085 | 2005-07-27 | DV | E-MIO | METC | 777 | 2005-07-27 | 89 | 2008-06-01 | Various | Capacitors |  | 138 |  | 72 Mvar |  | various | MI | 0 |  | 100 |  |  |  | Proposed | 2000000 | [8 empty] | Y | N | Y
1587 | 2006-07-05 | DV | East | METC | 1015 | 2005-08-12 | 131 | 2008-06-01 | Oden | Oden - New Capacitor | 1 | 138 |  | 21.6 Mvar | Oden - New 21.6 Mvar Capacitor |  | MI |  |  | 100 |  |  |  | Proposed | 510000 | Planning MISO |  |  | Delayed due to load growth. | 2005-08-12 | MTEP06 | METC - Russ Vente |  | Y | N | Y
1445 | 2005-07-27 | BR | E-MIO | METC | 743 | 2005-07-27 | 94 | 2008-12-31 | Thetford | Tittabawassee | 1 | 345 |  |  | relaying & communications | M7 | MI | 0 |  |  |  |  | 100 | Proposed | 2000000 | [8 empty] | Y | N | Y
1446 | 2005-07-27 | BR | E-MIO | METC | 743 | 2005-07-27 | 95 | 2008-12-31 | Tittabawassee | Nelson Road | 1 | 345 |  |  | relaying & communications | M7 | MI | 0 |  |  |  |  | 100 | Proposed | 2000000 | [8 empty] | Y | N | Y
1444 | 2005-07-27 | BR | E-MIO | METC | 743 | 2005-07-27 | 92 | 2008-12-31 | Hampton | Thetford | 2 | 345 |  |  | relaying & communications | M7 | MI | 0 |  |  |  |  | 100 | Proposed | 2000000 | [8 empty] | Y | N | Y
1443 | 2005-07-27 | BR | E-MIO | METC | 743 | 2005-07-27 | 91 | 2008-12-31 | Hampton | Thetford | 1 | 345 |  |  | relaying & communications | M7 | MI | 0 |  |  |  |  | 100 | Proposed | 2000000 | [8 empty] | Y | N | Y
1447 | 2005-07-27 | BR | E-MIO | METC | 743 | 2005-07-27 | 93 | 2008-12-31 | Hampton | Tittabawassee | 1 | 345 |  |  | relaying & communications | M7 | MI | 0 |  |  |  |  | 100 | Proposed | 1670000 |  | 18180000 | [6 empty] | Y | N | Y
1335 | 2006-03-16 | BR | E-MIO | METC | 650 | 2005-07-27 | 72 | 2009-05-01 | Battle Creek | Morrow | 1 | 138 |  |  |  | M7 | MI | 14.4 |  | 100 |  |  |  | Proposed | 3400000 |  |  |  | System Need Changed |  |  | METC - Russ Vente |  | Y | N | Y
1347 | 2005-07-27 | BR | E-MIO | METC | 660 | 2005-07-27 | 101 | 2009-05-01 | Keystone | Clearwater | 1 | 138 |  |  |  | M5 | MI | 23.2 |  | 100 |  |  |  | Proposed | 10200000 | [8 empty] | Y | N | Y
1351 | 2005-07-27 | BR | E-MIO | METC | 663 | 2005-07-27 | 105 | 2009-06-01 | METC | Various Distribution Connections | 1 | 138 |  |  |  | Various | MI |  | 1 | 100 |  |  |  | Proposed | 2000000 | [8 empty] | Y | N | Y
1544 | 2006-07-05 | BR | East | METC | 981 | 2005-07-27 | 63 | 2009-06-01 | Wabasis J. - N. Belding - Vergennes | Wabasis | 1 | 138 |  |  | Install aTap Pole and Switches |  | MI | [6 empty] | Planned | 160000 |  |  |  | Delayed due to load forecast reduction | 2005-07-27 | MTEP06 | METC - Russ Vente |  | Y | N | Y
1448 | 2005-07-27 | BR | E-MIO | METC | 744 | 2005-07-27 | 107 | 2009-12-31 | Argenta | Tallmadge | 1 | 345 |  |  | relaying & communications | M7 | MI | 0 |  |  |  |  | 100 | Proposed | 2000000 | [8 empty] | Y | N | Y
1449 | 2005-07-27 | BR | E-MIO | METC | 744 | 2005-07-27 | 110 | 2009-12-31 | Tallmadge | Kenowa | 1 | 345 |  |  | relaying & communications | M7 | MI | 0 |  |  |  |  | 100 | Proposed | 2000000 | [8 empty] | Y | N | Y
1450 | 2005-07-27 | BR | E-MIO | METC | 744 | 2005-07-27 | 109 | 2009-12-31 | Ludington | Tallmadge | 1&2 | 345 |  |  | relaying & communications | M7 | MI | 0 |  |  |  |  | 100 | Proposed | 2000000 | [8 empty] | Y | N | Y
1451 | 2005-07-27 | BR | E-MIO | METC | 744 | 2005-07-27 | 111 | 2009-12-31 | Tallmadge | Roosevelt | 1 | 345 |  |  | relaying & communications | M7 | MI | 0 |  |  |  |  | 100 | Proposed | 2000000 | [8 empty] | Y | N | Y
1452 | 2005-07-27 | BR | E-MIO | METC | 744 | 2005-07-27 | 108 | 2009-12-31 | Campbell | Tallmadge | 1 | 345 |  |  | relaying & communications | M7 | MI | 0 |  |  |  |  | 100 | Proposed | 1742000 |  | 25502000 | [6 empty] | Y | N | Y
1337 | 2006-03-16 | BR | E-MIO | METC | 651 | 2005-07-27 | 83 | 2010-05-01 | Stover | Clearwater | 1 | 138 |  |  |  | M5 | MI | 8.8 |  | 100 |  |  |  | Proposed | 2800000 |  |  |  | System Need Changed |  |  | METC - Russ Vente |  | Y | N | Y
1345 | 2006-03-16 | BR | E-MIO | METC | 658 | 2005-07-27 | 82 | 2010-05-01 | Gaylord | Livingston | 1 | 138 |  |  |  | M5 | MI | 1.5 |  | 100 |  |  |  | Proposed | 500000 |  |  |  | System Need Changed |  |  | METC - Russ Vente |  | Y | N | Y
1336 | 2005-11-28 | BR | E-MIO | METC | 480 | 2005-07-27 | 112 | 2010-06-01 | Brickyard J | Felch Road | 1 | 138 |  |  |  | M7 | MI | 12.8 |  | 100 |  |  |  | Proposed | 3000000 |  |  |  | System need changed (enabled delay) |  |  |  |  | Y | N | Y
1340 | 2006-03-16 | BR | E-MIO | METC | 654 | 2005-07-27 | 84 | 2010-06-01 | Almeda | Saginaw River | 1 | 138 |  |  |  | N6 | MI | 25 |  | 100 |  |  |  | Proposed | 6500000 |  |  |  | System Need Changed |  |  | METC - Russ Vente |  | Y | N | Y
1546 | 2005-07-27 | DV | E-MIO | METC | 983 | 2005-07-27 | 113 | 2010-12-31 | 345 kV line relaying and communications upgrade project - Phase 6 | 345 kV line relaying and communications upgrade project - Phase 6 |  | 345 |  |  |  |  | MI | [6 empty] | Proposed | 10000000 |  | 22800000 |  |  | 2005-07-27 | MTEP06 |  |  | Y | N | Y
336 | 2006-03-16 | BR | E-MIO | METC | 240 | 2005-07-27 | 87 | 2011-06-01 | Garfiled | Hemphill | 1 | 138 |  | 521 |  | N7 | MI | 9.2 |  | 100 |  |  |  | Proposed | 1900000 |  |  |  | Low system need |  |  | METC - Russ Vente |  | Y | N | Y | METC_2011Sum_U2_8-12-2005_29.idv
1547 | 2005-07-27 | BR | E-MIO | METC | 984 | 2005-07-27 | 114 | 2011-06-01 | Denver Station | New Station |  | 345 |  |  | New Station |  | MI | [6 empty] | Proposed | 77132000 | Planning MISO |  |  |  | 2005-07-27 | MTEP06 |  |  | Y | N | Y
1551 | 2005-07-27 | BR | E-MIO | METC | 988 | 2005-07-27 | 120 | 2011-06-01 | Simpson | Batavia | 1 | 138 |  |  |  |  | MI |  | 30 |  |  |  |  | Proposed | 13000000 |  |  |  |  | 2005-07-27 | MTEP06 |  |  | Y | N | Y
1554 | 2006-07-05 | BR | East | METC | 991 | 2005-07-27 | 127 | 2011-06-01 | Argentine - CE Lovejoy | Argentine - (NDS) - No METC Facility | 1 | 138 | 24.9 |  |  |  | MI | [6 empty] | Planned | 0 |  |  |  | Delayed due to load growth. | 2005-07-27 | MTEP06 | METC - Russ Vente |  | Y | N | Y
1548 | 2005-07-27 | DV | E-MIO | METC | 985 | 2005-07-27 | 115 | 2011-12-31 | 345 kV line relaying and communications upgrade project - Phase 7 | 345 kV line relaying and communications upgrade project - Phase 7 |  | 345 |  |  |  |  | MI | [6 empty] | Proposed | 10000000 |  | 102032000 |  |  | 2005-07-27 | MTEP06 |  |  | Y | N | Y
1334 | 2006-03-16 | BR | E-MIO | METC | 649 | 2005-07-27 | 81 | 2012-05-01 | Argenta | Palisades(Sag) | 1&2 | 345 |  |  | conductor sag | M7 | MI | 0.1 |  | 100 |  |  |  | Proposed | 500000 |  |  |  | System Need Changed |  |  | METC - Russ Vente |  | Y | N | Y
1549 | 2005-07-27 | DV | E-MIO | METC | 986 | 2005-07-27 | 116 | 2012-12-31 | 345 kV line relaying and communications upgrade project - Phase 8 | 345 kV line relaying and communications upgrade project - Phase 8 |  | 345 |  |  |  |  | MI | [6 empty] | Proposed | 10000000 |  | 10500000 |  |  | 2005-07-27 | MTEP06 |  |  | Y | N | Y
1350 | 2005-11-28 | BR | E-MIO | METC | 662 | 2005-07-27 | 117 | 2013-05-01 | Weeds Lake 345 | Weeds Lake 138 | 1 | 345 | 138 |  |  | M7 | MI |  | 10 | 100 |  |  |  | Proposed | 13000000 |  |  |  | System need changed (enabled delay) |  |  |  |  | Y | N | Y
1550 | 2005-07-27 | BR | E-MIO | METC | 987 | 2005-07-27 | 118 | 2013-06-01 | Emmet | Stover | 1 | 138 |  |  |  |  | MI | [6 empty] | Proposed | 10250000 |  | 23250000 |  |  | 2005-07-27 | MTEP06 |  |  | Y | N | Y
1925 | 2005-11-28 | BR | E-MIO | METC | 1225 | 2005-11-28 | 98 | 2015-05-01 | Thompson Road | Tallman | 1 | 138 |  |  |  | M7 | MI | 19.2 |  | 100 |  |  |  | Proposed | 5000000 |  |  |  | Replacement for David-Bingham 138 kV (Project 656) |  |  |  |  | Y | N | Y
1325 | 2006-07-05 | BR | East | METC | 642 | 2005-07-27 | 57 | 2017-06-01 | Argenta | Hazelwood(Sag) | 1 | 138 |  |  | conductor sag | M7 | MI | 0.1 |  | 100 |  |  |  | Proposed | 50000 |  |  |  | No current system need |  |  | METC - Russ Vente |  | Y | N | Y
3018 | 2005-07-11 | DV | N-NM | MH | 442 | 2006-03-24 | 442 | 2006-10-31 | Portage South | Capacitor |  | 66 |  | 3 x 10 |  | F2 | Manitoba |  |  | 40 | 20 | 40 |  | Proposed | 1117775.4274 | Engineering | [7 empty] | Y | Y | Y
239 | 2006-03-24 | BR | N-NM | MH | 604 | 2006-03-24 | 604 | 2006-11-01 | Herblet Lake | Sherridon | 1 | 115 |  | 63 | Upgrade of old line | Manitoba | Manitoba | 45.3 |  |  |  |  | 100 | Proposed | 7835115.4839 | Engineering | 8952890.9113 |  | Budget deferral |  |  | MH - David Diakiw |  | Y | Y | Y
562 | 2006-06-28 | BR | N-NM | MH | 264 | 2006-03-24 | 264 | 2007-03-31 | Birchtree | Wuskwatim | 1 | 230 |  | 390 | New generation transmission | Manitoba | Manitoba |  | 28 |  | 100 |  |  | Planned | 13495431.77 | Engineering |  |  | Delays in Final Approval, ISD adjusted |  |  | MH - David Diakiw |  | Y | Y | Y
962 | 2006-06-28 | BR | N-NM | MH | 917 | 2006-06-28 | 7 | 2007-03-31 | St Vital | Scotland | 1 | 115 |  | 110 | Reconfigure line (originally VH2) | Manitoba | Manitoba | 0 |  | 100 |  |  |  | Proposed | 198176.12 | Engineering |  |  | Line is swapped in field with ID 963 | 2005-07-11 | MTEP06 | MH - David Diakiw |  | Y | Y | Y
963 | 2006-06-28 | BR | N-NM | MH | 917 | 2006-06-28 | 7 | 2007-03-31 | Mohawk | Harrow | 1 | 115 |  | 80 | Reconfigure line (originally XS49) | Manitoba | Manitoba | 0 |  | 100 |  |  |  | Proposed | 286288.45 | Engineering |  |  | Line is swapped in field with ID 962 | 2005-07-11 | MTEP06 | MH - David Diakiw |  | Y | Y | Y
961 | 2006-06-28 | BR | N-NM | MH | 917 | 2006-06-28 | 7 | 2007-03-31 | LaVerendrye(YV5) | St Vital | 1 | 115 |  | 178.9 | Reconductor section of line | Manitoba | Manitoba |  | 1.88 | 100 |  |  |  | Proposed | 198176.12 | Engineering |  |  |  | 2005-07-11 | MTEP06 | MH - David Diakiw |  | Y | Y | Y
958 | 2005-07-11 | BR | N-NM | MH | 915 | 2006-06-28 | 5 | 2007-04-30 | Rosser 230-115 kV | transformer | 2 | 230 | 115 | 250 | transformer upgrade 176 to 250 mva | F2 | Manitoba |  |  | 100 |  |  |  | Proposed | 2464590.2617 | Engineering |  |  | 67582 | 2005-07-11 | MTEP06 |  |  | Y | Y | Y
956 | 2005-07-11 | BR | N-NM | MH | 913 | 2006-06-28 | 3 | 2007-11-01 | Richer South 230-63.5 kV | transformer | 2 | 230 | 63.5 | 93 | transformer addition | F2 | Manitoba |  |  | 100 |  |  |  | Planned | 7251831.0317 | Engineering | 23894493.7534 |  |  | 2005-07-11 | MTEP06 |  |  | Y | Y | Y
1240 | 2006-03-24 | BR | N-NM | MH | 604 | 2006-03-24 | 604 | 2008-03-01 | Herblet Lake | Chisel Lake | 1 | 115 |  | 98 | New transmission to feed load | Manitoba | Manitoba |  | 3.7 | 100 |  |  |  | Proposed | 3628560.1755 | Engineering | 3628560.1755 |  | Budget deferral |  |  | MH - David Diakiw |  | Y | Y | Y
964 | 2005-07-11 | BR | N-NM | MH | 557 | 2005-07-11 | 557 | 2009-11-01 | Court transformer #2 | transformer | 1 | 115 | 7.2 | 58 | companion bank | F2 | Manitoba |  |  | 100 |  |  |  | Planned | 7468772.9113 | Engineering |  |  | 67560 | 2005-07-11 | MTEP06 |  |  | Y | Y | Y
1089 | 2005-07-11 | BR | N-NM | MH | 914 | 2006-06-28 | 4 | 2009-11-01 | Ridgeway 230-63.5 kV | transformer | 3 | 230 | 63.5 | 140 | transformer addition | F2 | Manitoba |  |  | 100 |  |  |  | Proposed | 7468772.9113 | Engineering | 14937545.8226 | [6 empty] | Y | Y | Y
959 | 2005-07-11 | BR | N-NM | MH | 912 | 2006-06-28 | 2 | 2010-05-01 | Point du Bois | Rover | 1 | 115 |  | 125 | replacing two existing old 66 kV lines | Manitoba | Manitoba | 75 |  |  | 100 |  |  | Proposed | 24803532.3607 | Engineering |  |  |  | 2005-07-11 | MTEP06 |  |  | Y | Y | Y
2078 | 2006-03-24 | DV | N-NM | MH | 442 | 2006-03-24 | 442 | 2010-10-31 | Brandon | Capacitor |  | 115 |  | 54 |  | F2 | Manitoba |  |  | 40 | 20 | 40 |  | Planned | 472909.3548 | Engineering |  |  | Lower than expected load growth, ISD adjusted |  |  | MH - David Diakiw |  | Y | Y | Y
1091 | 2006-06-28 | BR | N-NM | MH | 264 | 2006-03-24 | 264 | 2010-11-30 | Herblet Lake | Wuskwatim | 2 | 230 |  | 390 | New generation transmission | Manitoba | Manitoba |  | 86 |  | 100 |  |  | Planned | 31106922.56 | Engineering |  |  | Delays in Final Approval, ISD adjusted |  |  | MH - David Diakiw |  | Y | Y | Y
1090 | 2006-06-28 | BR | N-NM | MH | 264 | 2006-03-24 | 264 | 2010-11-30 | Herblet Lake | Wuskwatim | 1 | 230 |  | 390 | New generation transmission | Manitoba | Manitoba |  | 86 |  | 100 |  |  | Planned | 31106922.56 | Engineering | 87490286.8355 |  | Delays in Final Approval, ISD adjusted |  |  | MH - David Diakiw |  | Y | Y | Y
580 | 2005-07-11 | BR | N-NM | MH | 288 | 2006-03-24 | 288 | 2011-08-01 | Riel Stn 500-230 kV | transformer | 1 | 500 | 230 | 1200 | New station and transformation for future Bipole | F2 | Manitoba |  |  |  | 100 |  |  | Proposed | 2756010.629 | Engineering | [7 empty] | Y | Y | Y
2089 | 2006-06-28 | DV | N-NM | MH | 264 | 2006-03-24 | 264 | 2011-08-31 | Thompson Birchtree | SVC |  | 230 |  | 150/-20 | New generation transmission |  | Manitoba |  |  |  | 100 |  |  | Planned | 16538691.05 | Engineering |  |  | Delays in Final Approval, ISD adjusted |  |  | MH - David Diakiw |  | Y | Y | Y
1092 | 2006-06-28 | BR | N-NM | MH | 264 | 2006-03-24 | 264 | 2011-10-31 | Herblet Lake | Ralls Island | 1 | 230 |  | 390 | New generation transmission | Manitoba | Manitoba |  | 103 | 50 | 50 |  |  | Planned | 36924629.44 | Engineering |  |  | Delays in Final Approval, ISD adjusted |  |  | MH - David Diakiw |  | Y | Y | Y
955 | 2005-07-11 | BR | N-NM | MH | 1013 | 2006-06-28 | 1 | 2011-10-31 | Neepawa | Dorsey | 1 | 230 |  | 432 | Sectionalize line to feed new 230 - 66 kV station | Manitoba | Manitoba | 0 |  | 100 |  |  |  | Proposed | 16462591.9541 | Engineering |  |  |  | 2005-07-11 | MTEP06 |  |  | Y | Y | Y
954 | 2005-07-11 | BR | N-NM | MH | 1013 | 2006-06-28 | 1 | 2011-10-31 | Neepawa | Cornwallis | 1 | 230 |  | 432 | Sectionalize line to feed new 230 - 66 kV station | Manitoba | Manitoba | 0 |  | 100 |  |  |  | Proposed | 16462591.9541 | Engineering |  |  |  | 2005-07-11 | MTEP06 |  |  | Y | Y | Y
1100 | 2005-07-11 | BR | N-NM | MH | 291 | 2006-03-24 | 291 | 2011-11-01 | Loon Straights | Bloodvein | 1 | 115 |  | 93 | Replacement/new of existing 66 kV to 115 kV | Manitoba | Manitoba | 54.9 | 34 | 100 |  |  |  | Proposed | 18665777.6452 | Engineering | [7 empty] | Y | Y | Y
1101 | 2005-07-11 | BR | N-NM | MH | 291 | 2006-03-24 | 291 | 2011-11-01 | Pine Falls | Loon Straights | 1 | 115 |  | 93 | Replacement/new of existing 66 kV to 115 kV | Manitoba | Manitoba |  | 10.7 |  | 100 |  |  | Proposed | 4441382.3732 | Engineering | 112251675.0456 | [6 empty] | Y | Y | Y
242 | 2005-07-11 | BR | N-NM | MH | 98 | 2006-03-24 | 77 | 2012-11-01 | Ridgeway | Selkirk | 1 | 230 |  | 476 |  | G2 | Manitoba |  | 14.3 | 100 |  |  |  | Proposed | 1654807.7275 | [8 empty] | Y | Y | Y
243 | 2005-07-11 | BR | N-NM | MH | 98 | 2006-03-24 | 77 | 2012-11-02 | Selkirk 230-115 kV | transformer | 1 | 230 | 115 | 250 |  | Manitoba | Manitoba |  |  | 100 |  |  |  | Proposed | 876923.1978 |  | 2531730.9253 | [6 empty] | Y | Y | Y
581 | 2005-07-11 | BR | N-NM | MH | 278 | 2006-03-24 | 273 | 2013-11-01 | Dorsey | Portage South | 2 | 230 |  | 384 |  | F2 | Manitoba |  | 43.5 | 100 |  |  |  | Proposed | 17923199.6774 |  | 17923199.6774 | [6 empty] | Y | Y | Y
1096 | 2005-12-22 | BR | N-NM | MH | 289 | 2006-06-28 | 284 | 2017-10-01 | Henday (dc) | Riel (dc) | 1 | 500 |  | 2000 | direct current line | Manitoba | Manitoba |  | 513 |  | 100 |  |  | Proposed | 398746149.0174 |  | 398746149.0174 |  | Re-evaluating other options due to environmental road blocks |  |  |  |  | Y | Y | Y
1094 | 2006-03-24 | BR | N-NM | MH | 283 | 2006-03-24 | 283 | 2020-05-30 | Rosser | Oak Point Tap | 1 | 115 |  | 110.1 | new 115-24 kV station with two banks | F2 | Manitoba | 6.6 |  | 100 |  |  |  | Proposed | 940331.2745 | Engineering |  |  | Lower than expected load growth, ISD adjusted |  |  | MH - David Diakiw |  | Y | Y | Y
1093 | 2006-03-24 | BR | N-NM | MH | 283 | 2006-03-24 | 283 | 2020-05-30 | Oak Point Tap | Augier | 1 | 115 |  | 110.1 | new 115-24 kV station with two banks | F2 | Manitoba | 6.6 |  | 100 |  |  |  | Proposed | 940331.2745 | Engineering |  |  | Lower than expected load growth, ISD adjusted |  |  | MH - David Diakiw |  | Y | Y | Y
1097 | 2006-03-24 | BR | N-NM | MH | 285 | 2006-06-28 | 280 | 2020-11-01 | St. Vital | Steinbach | 1 | 230 |  | 399 |  | F2 | Manitoba |  | 35 | 100 |  |  |  | Proposed | 13653801.9165 |  | 15534464.4655 |  | Lower than expected load growth, ISD adjusted |  |  | MH - David Diakiw |  | Y | Y | Y
318 | 2003-06-03 | BR | N-NM | MP | 1 | 2005-07-11 | 1 | 2008-06-30 | Arrowhead 230-230 kV | Phase-Shifter | 1 | 230 | 230 | 800 |  | I4 | MN |  |  | 50 |  | 25 | 25 | Planned | 13741772.8 | [5 empty] | MTEP03 |  |  | Y | Y | Y
319 | 2003-06-03 | BR | N-NM | MP | 1 | 2005-07-11 | 1 | 2008-06-30 | Arrowhead 345/230 kV | transformer | 1 | 345 | 230 | 800 |  | I4 | MN |  |  | 50 |  | 25 | 25 | Planned | 10400000 | [5 empty] | MTEP03 |  |  | Y | Y | Y
2039 | 2003-06-03 | DV | N-NM | MP | 1 | 2005-07-11 | 1 | 2008-06-30 | Arrowhead | Capacitor |  | 230 |  | 4 x 40 Mvar |  | I4 | MN |  |  | 100 |  |  |  | Planned | 1858227.2 | [5 empty] | MTEP03 |  |  | Y | Y | Y
579 | 2004-01-29 | BR | N-NM | MP | 277 | 2005-06-15 |  | 2008-06-30 | Badoura | Pequot Lakes | 1 | 115 |  | 182 |  | H4 | MN |  | 30 | 100 |  |  |  | Proposed | 7500000 | [8 empty] | Y | Y | Y
1590 | 2005-08-29 | BR | N-NM | MP/GRE | 1021 | 2005-08-29 |  | 2008-11-01 | Embarrass 115 | Tower 115 | 1 | 115 |  | 182 | New 115 kV line |  | MN |  | 15 | 100 |  |  |  | Proposed | 7314000 | Planning MISO | 40814000 |  |  | 2005-08-29 | MTEP06 |  |  | Y | Y | Y
1591 | 2005-08-29 | BR | N-NM | MP/GRE | 1022 | 2005-08-29 |  | 2009-11-01 | Badoura 115 | Long Lake 115 | 1 | 115 |  | 182 | New 115 kV line |  | MN |  | 17 | 100 |  |  |  | Proposed | 8621000 | Planning MISO |  |  |  | 2005-08-29 | MTEP06 |  |  | Y | Y | Y
1098 | 2005-07-29 | BR | N-NM | MPC/XEL/OTP/MP | 279 | 2005-07-29 | CAPX Group 1 | 2010-07-01 | Boswell | Wilton | 1 | 230 |  | 390 | Add a new 230 kV line between Boswell and Wilton | H4 | MN |  | 85 | 100 |  |  |  | Proposed | 35963293 | Planning |  |  | Is this same as Bemidji - Boswell 230 kV line? |  |  |  |  | Y | Y | Y
966 | 2006-06-30 | BR | E-MIO | NIPS | 920 | 2006-06-30 | 71C6113 | 2006-07-07 | Hiple | transformer | 2 | 138 | 69 | 112 | Add 2nd 138/69 kV Transformer | M8 | IN |  |  | 100 |  |  |  | Planned | 2446300 | Engineering w AFUDC |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
967 | 2006-06-30 | BR | E-MIO | NIPS | 921 | 2006-06-30 | 71C6307 | 2006-07-11 | Goodland | Transformer | 1 | 138 | 69 | 112 | Replace #1 Transformer - Increase Capacity |  | IN |  |  | 100 |  |  |  | Planned | 1613500 | Engineering w AFUDC |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
969 | 2006-06-30 | DV | E-MIO | NIPS | 926 | 2006-06-30 | 9325540 | 2006-08-01 | Monticello | Capacitor |  | 69 |  |  | Add Capacitors - (4) 10.8 MVAR steps |  | IN |  |  | 100 |  |  |  | Planned | 1307500 | Engineering w AFUDC |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
970 | 2006-06-30 | BR | E-MIO | NIPS | 925 | 2006-06-30 | 71C6613 | 2006-12-01 | ISG2 | Marktown | 1 | 138 |  | 316 | Upgrade Connections and Circuit |  | IN | 0.6 |  |  |  |  | 100 | Planned | 240500 | Engineering w AFUDC | 5607800 |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
3034 | 2006-06-30 | DV | E-MIO | NIPS | 757 | 2006-06-30 | 9320027 | 2007-02-01 | Dune Acres | Capacitor |  | 138 |  |  | Add Capacitor - (1) 100 MVAR step | L8 | IN |  |  | 100 |  |  |  | Planned | 1083600 | Engineering w AFUDC |  |  | Slower load growth than initially projected |  |  |  |  | Y | N | Y
971 | 2006-06-30 | BR | E-MIO | NIPS | 922 | 2006-06-30 | 71C6331 | 2007-05-01 | Michigan City | Luchtman Road | 1 | 138 |  | 316 | Upgrade circuit capacity |  | IN | 5 |  | 100 |  |  |  | Proposed | 1705400 | Engineering w AFUDC |  |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
972 | 2006-06-30 | BR | E-MIO | NIPS | 923 | 2006-06-30 | 71C6602 | 2007-05-01 | Plymouth | Transformer | 3 | 138 | 69 | 168 | Add 3rd 138/69 kV Transformer |  | IN |  |  | 100 |  |  |  | Proposed | 2689400 | Engineering w AFUDC | 4394800 |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1279 | 2006-06-30 | BR | E-MIO | NIPS | 612 | 2006-06-30 | 9325101 | 2008-05-01 | Hiple | transformer | 2 | 345 | 138 | 560 | Add 2nd 345/138 kV Transformer | M8 | IN |  |  | 100 |  |  |  | Proposed | 3992400 | Planning w AFUDC | [7 empty] | Y | N | Y
974 | 2006-06-30 | BR | E-MIO | NIPS | 919 | 2006-06-30 | 9320020 | 2008-12-01 | Lagrange | Transformer | 1 | 138 | 69 | 168 | Replace #1 Transformer - Increase Capacity | M8 | IN |  |  | 100 |  |  |  | Proposed | 1593300 | Planning w AFUDC | 5585700 |  |  | 2005-07-08 | MTEP06 |  |  | Y | N | Y
1530 | 2005-07-29 | DV | N-NM | OTP | 549 | 2005-07-29 |  | 2007-12-31 | Jamestown | Reactor |  | 115 |  | 25 Mvar | Add a 1 x 25 MVAr reactor at OTP Jamestown substation | E4 | ND |  |  | 100 |  |  |  | Proposed | 436672 | Planning | [7 empty] | Y | Y | Y
377 | 2006-03-27 | BR | N-NM | OTP | 274 | 2005-07-29 |  | 2008-12-31 | Appleton | Dawson | 1 | 115 |  | 96 | Convert an existing 41.6 kV line to 115 kV | G5 | MN | 21.3 |  | 100 |  |  |  | Planned | 464681 | Planning |  |  | Permitting Efforts within MN are behind schedule |  |  | OTP - Jason Weiers |  | Y | Y | Y
378 | 2006-03-27 | BR | N-NM | OTP | 275 | 2005-07-29 |  | 2008-12-31 | Dawson | Canby | 1 | 115 |  | 96 | Convert an existing 41.6 kV line to 115 kV | G5 | MN | 21.1 |  | 100 |  |  |  | Planned | 460318 | Planning | 924999 |  | Permitting Efforts within MN are behind schedule |  |  | OTP - Jason Weiers |  | Y | Y | Y
1523 | 2005-11-01 | BR | N-NM | OTP | 973 | 2005-11-01 |  | 2010-07-01 | Canby 230/115 kV | transformer |  | 230 | 115 | 336 | Install a 230/115 kV Transformer for Big Stone II Generation Outlet (Alternative 1 and 2) | F6 | MN |  |  |  | 100 |  |  | Planned | 6100000 | Planning |  |  |  | 2005-07-29 | MTEP06 |  | G392 | Y | Y |  | Network
1521 | 2005-11-01 | BR | N-NM | OTP | 973 | 2005-11-01 |  | 2010-07-01 | Big Stone 230 | Canby 230 | 1 | 230 |  | 1145 | Build new 230 kV line with 2-1272 ACSR for Big Stone II Generation Outlet (Alternative 1 and 2) | F6 | MN/SD |  | 55 |  | 100 |  |  | Planned | 41250000 | Planning |  |  |  | 2005-07-29 | MTEP06 |  | G392 | Y | Y |  | Network
1525 | 2005-11-01 | BR | N-NM | OTP | 973 | 2005-11-01 |  | 2010-07-01 | Morris 230/115 kV | transformer |  | 230 | 115 | 336 | Replace existing transformer at Morris with 336 MVA unit (Required Int. upgrade for Alternative 1) | F6 | MN |  |  |  | 100 |  |  | Planned | 6100000 | Planning |  |  |  | 2005-07-29 | MTEP06 |  | G392 | Y | Y |  | Interconnection
1522 | 2005-11-01 | BR | N-NM | OTP | 973 | 2005-11-01 |  | 2010-07-01 | Canby 230 | Granite Falls 230 | 1 | 230 |  | 1145 | Build new 230 kV line with 2-1272 ACSR for Big Stone II Generation Outlet (Alternative 1 and 2) | F6 | MN | 39.2 |  |  | 100 |  |  | Planned | 29400000 | Planning |  |  |  | 2005-07-29 | MTEP06 |  | G392 | Y | Y |  | Network
1515 | 2005-11-01 | BR | N-NM | OTP | 973 | 2005-11-01 |  | 2010-07-01 | Big Stone 230 | Ortonville 230 | 1 | 230 |  | 520 | Build new 230 kV line with 1272 ACSR for Big Stone II Generation Outlet (Alternative 1) | F6 | MN/SD |  | 6.5 |  | 100 |  |  | Planned | 2400000 | Planning |  |  |  | 2005-07-29 | MTEP06 |  | G392 | Y | Y |  | Network
1517 | 2005-11-01 | BR | N-NM | OTP | 973 | 2005-11-01 |  | 2010-07-01 | Johnson Jct. 230 | Morris 230 | 1 | 230 |  | 520 | Convert existing 115 kV line to 230 kV with 1272 ACSR for Big Stone II Generation Outlet (Alternative 1) | F6 | MN | 15.4 |  |  | 100 |  |  | Planned | 9400000 | Planning |  |  |  | 2005-07-29 | MTEP06 |  | G392 | Y | Y |  | Network
1516 | 2005-11-01 | BR | N-NM | OTP | 973 | 2005-11-01 |  | 2010-07-01 | Ortonville 230 | Johnson Jct. 230 | 1 | 230 |  | 520 | Convert existing 115 kV line to 230 kV with 1272 ACSR for Big Stone II Generation Outlet (Alternative 1) | F6 | MN | 24.6 |  |  | 100 |  |  | Planned | 15100000 | Planning |  |  |  | 2005-07-29 | MTEP06 |  | G392 | Y | Y |  | Network
1524 | 2005-11-01 | BR | N-NM | OTP | 973 | 2005-11-01 |  | 2010-07-01 | Big Stone 230 | Browns Valley 230 kV |  | 230 |  | 390 | Upgrade substation equipment at Browns Valley to achieve rating equal to thermal rating of line (Required Int. upgrade for Alts 1 and 2) | F6 | SD | 38.7 |  |  | 100 |  |  | Planned | 2000000 | Planning |  |  |  | 2005-07-29 | MTEP06 |  | G392 | Y | Y |  | Interconnection
1518 | 2005-11-01 | BR | N-NM | OTP | 973 | 2005-11-01 |  | 2010-07-01 | Johnson Jct. 230/115 kV | transformer | 1 | 230 | 115 | 112 | Install a 230/115 kV Transformer for Big Stone II Generation Outlet (Alternative 1) | F6 | MN |  |  |  | 100 |  |  | Planned | 3000000 | Planning | 114750000 |  |  | 2005-07-29 | MTEP06 |  | G392 | Y | Y |  | Network
589 | 2005-07-29 | BR | N-NM | OTP | 585 | 2006-03-27 |  | 2017-06-01 | Pelican Rapids | Pelican Rapids Turkey Plant | 1 | 115 |  | 85 | Convert an existing 41.6 kV line to 115 kV | G4 | MN | 2.5 |  | 100 |  |  |  | Planned | 858869 | Planning |  |  | Long-term Planned |  |  |  |  | Y | Y | Y
235 | 2006-03-27 | BR | N-NM | OTP/MPC | 971 | 2005-07-29 | OTP1 | 2010-12-31 | Winger 230-115 kV | transformer | 1 | 230 | 115 | 187 | Final Design not yet complete - Either add a 2nd 230/115 kV TX or else replace existing 187 MVA transformer with something larger | G4 | MN |  |  | 100 |  |  |  | Proposed | 3715350.8388 | Planning |  |  | Proposed Boswell - Wilton 230 kV line adversely effects loading on transformer. In-service date changed to align with Boswell - Wilton 230 kV line. |  |  | OTP - Jason Weiers |  | Y | Y | Y
2077 | 2006-03-27 | DV | N-NM | OTP/MRES/GRE | 441 | 2005-07-29 |  | 2007-06-01 | Alexandria Poleyard Municipal | Capacitors |  | 115 |  | 25 Mvar | Add a 1 x 25 MVAr capacitor bank at the Alexandria Poleyard substation | G5 | MN |  |  | 100 |  |  |  | Planned | 530000 | Planning | [5 empty] | OTP - Jason Weiers |  | Y | Y | Y
3032 | 2006-03-27 | DV | N-NM | OTP/MRES/GRE | 755 | 2005-07-29 |  | 2007-06-01 | Alexandria Switching Station | Capacitors |  | 115 |  | 25 Mvar | Add a 1 x 25 MVAr capacitor bank at the Alexandria Switching Station | G5 | MN |  |  | 100 |  |  |  | Planned | 530000 | Planning | [5 empty] | OTP - Jason Weiers |  | Y | Y | Y
60 | 2005-11-28 | BR | C-CSILL | SIPC | 81 | 2005-06-15 | 57 | 2007-06-01 | Marion | CarrierMills | 1 | 161 |  | 286 |  | K11 | IL |  | 27 | 100 |  |  |  | Planned | 7083000 |  |  |  | ROW - Condemnation |  | MTEP03 |  |  | Y | N
1562 | 2006-06-29 | BR | E-IOK | Vectren | 998 | 2005-07-28 |  | 2006-08-01 | Elliott | transformer | 2 | 138 | 69 | 53/'60 | used transformer from Newtonville | L11 | IN |  |  | 100 |  |  |  | Under Construction | 600000 | Budgetary |  |  | No increased risk. Project ahead of load growth. | 2005-07-28 | MTEP06 | Vectren - Fred Fredrick |  | Y | N | Y
381 | 2006-03-16 | BR | E-IOK | Vectren | 182 | 2006-03-16 |  | 2006-11-30 | Newtonville 161/138 (SIGE) | transformer | 2 | 161 | 138 | 168 |  | M11 | IN |  |  |  |  | 50 | 50 | Planned | 2280000 | [6 empty] | Vectren - Fred Fredrick |  | Y | N | Y
1569 | 2006-06-29 | BR | E-IOK | Vectren | 1004 | 2006-06-29 | 2.1 2.2 2.5 2.6 | 2007-05-31 | Francisco 345/138 kV | Substation | 1 | 345 | 138 | 896/940 | new substation with two 345/138 transformers and 345 kV interconnection with Cinergy on Gibson-Duff line | L11 | IN |  |  | 25 |  | 25 | 50 | Planned | 13225000 | Budgetary |  |  | Formerly known as Snake Run. Each transformer rated 448/470 | 2005-07-28 | MTEP06 | Vectren - Fred Fredrick |  | Y | N | Y
1570 | 2006-06-29 | BR | E-IOK | Vectren | 1005 | 2006-06-29 | 2.4 3.2 3.4 3.6 | 2007-05-31 | Francisco | Northeast | 76 | 138 |  | 287/287 | new line | L11 | IN |  | 31 | 25 |  | 25 | 50 | Planned | 10900000 | Budgetary |  |  | Formerly known as Snake Run to Northeast | 2005-07-28 | MTEP06 | Vectren - Fred Fredrick |  | Y | N | Y
1571 | 2006-06-29 | BR | E-IOK | Vectren | 1005 | 2006-06-29 | 2.3 3..3 3.5 3.6 | 2007-05-31 | Francisco | Northwest | 75 | 138 |  | 287/287 | new line | L11 | IN |  | 31 | 25 |  | 25 | 50 | Planned | 10200000 | Budgetary |  |  | Formerly known as Snake Run to Northwest | 2005-07-28 | MTEP06 | Vectren - Fred Fredrick |  | Y | N | Y
1974 | 2006-06-29 | BR | E-IOK | Vectren | 1258 | 2006-06-29 | 7.1 7.2 7.3 7.4 | 2007-05-31 | Pigeon Creek 138/69 kV | transformer | 1 | 138 | 69 | 168/176 | new transformer with tie ins for 138 kV and 69 kV lines | L11 | IN |  |  | 100 |  |  |  | Planned | 3400000 | Budgetary |  |  |  | 2006-06-29 | MTEP06 | Vectren - Fred Fredrick |  | Y | N | Y
1975 | 2006-06-29 | BR | E-IOK | Vectren | 1259 | 2006-06-29 | 1.1 1.2 1.3 | 2007-05-31 | Dubois | Newtonville | 78 | 138 |  | 287/287 | new line | M11 | IN | 28 |  | 100 |  |  |  | Planned | 14400000 | Budgetary | 38900000 |  |  | 2006-06-29 | MTEP06 | Vectren - Fred Fredrick |  | Y | N | Y
1565 | 2006-06-29 | BR | E-IOK | Vectren | 1001 | 2006-06-29 | 6.1 | 2008-05-31 | Oak Grove 138/69 kV | transformer | 1 | 138 | 69 | 168/176 | new transformer | L11 | IN |  |  | 100 |  |  |  | Planned | 3400000 | Budgetary |  |  |  | 2005-07-28 | MTEP06 | Vectren - Fred Fredrick |  | Y | N | Y
1567 | 2006-06-29 | BR | E-IOK | Vectren | 1002 | 2006-06-29 | 6.2 | 2008-05-31 | Oak Grove | Culley | 77 | 138 |  | 287/287 | new line | L11 | IN |  |  | 100 |  |  |  | Planned | 4250000 | Budgetary |  |  |  | 2005-07-28 | MTEP06 | Vectren - Fred Fredrick |  | Y | N | Y
1559 | 2006-06-29 | BR | E-IOK | Vectren | 995 | 2006-06-29 |  | 2008-12-31 | Mount Vernon | transformer | 1 | 138 | 69 | 67/76 | add 2nd transformer from reserve equipment | L11 | IN |  |  | 100 |  |  |  | Proposed | 50000 | Budgetary |  |  |  | 2005-07-28 | MTEP06 | Vectren - Fred Fredrick |  | Y | N | Y
1566 | 2006-06-29 | BR | E-IOK | Vectren | 1002 | 2006-06-29 | 6.3 | 2008-12-31 | Northeast | Oak Grove | 77 | 138 |  | 287/287 | new line | L11 | IN |  |  | 100 |  |  |  | Planned | 4250000 | Budgetary | 11950000 |  |  | 2005-07-28 | MTEP06 | Vectren - Fred Fredrick |  | Y | N | Y
1968 | 2006-06-29 | BR | E-IOK | Vectren | 1005 | 2006-06-29 | 3.1 3.8 3.9 3.10 3.11 3.12 | 2009-05-31 | Blue Grass 138/69 kV | Substation |  | 138 | 69 | 168/176 | new substation with one 138/69 kV transformer and 138 & 69 kV tie ins | L11 | IN |  |  | 50 |  |  | 50 | Planned | 10000000 | Budgetary | [5 empty] | Vectren - Fred Fredrick |  | Y | N | Y
1969 | 2006-06-29 | BR | E-IOK | Vectren | 1005 | 2006-06-29 | 3.7 | 2009-05-31 | Blue Grass | Elliott | 74 | 138 |  | 287/287 | new line | L11 | IN |  | 6 | 50 |  |  | 50 | Planned | 3900000 | Budgetary | [5 empty] | Vectren - Fred Fredrick |  | Y | N | Y
1575 | 2006-06-29 | BR | E-IOK | Vectren | 1007 | 2006-06-29 | 5.3 | 2009-12-31 | Culley 345/138 kV | transformer | 1 | 345 | 138 | 448/470 | New 345 bus & transformer | L11 | IN |  |  |  |  | 50 | 50 | Planned | 5400000 | Budgetary |  |  |  | 2005-07-28 | MTEP06 | Vectren - Fred Fredrick |  | Y | N | Y
1970 | 2006-06-29 | BR | E-IOK | Vectren | 1007 | 2006-06-29 | 5.1 5.2 | 2009-12-31 | Culley | Duff | 11 | 345 |  | 1430/1430 | new line | L11 | IN | 33 |  |  |  | 50 | 50 | Planned | 24750000 | Budgetary |  |  |  | 2006-06-29 | MTEP06 | Vectren - Fred Fredrick |  | Y | N | Y
1574 | 2006-06-29 | BR | E-IOK | Vectren | 1007 | 2006-06-29 | 5.4 5.5 | 2009-12-31 | Culley | Smith (OMU) | 12 | 345 |  | 1430/1430 | New interconnection to new Owensboro Municipal Station | M11 | IN/KY |  | 20 |  |  | 50 | 50 | Planned | 21750000 | Budgetary | 65800000 |  |  | 2005-07-28 | MTEP06 | Vectren - Fred Fredrick |  | Y | N | Y
1973 | 2006-06-29 | BR | E-IOK | Vectren | 1257 | 2006-06-29 | 8.4 8.5 | 2011-05-31 | AB Brown | Reid (BREC) | 17 | 345 |  | 1430/1430 | new line | L11 | IN/KY |  | 24 |  |  | 50 | 50 | Planned | 26050000 | Budgetary |  |  |  | 2006-06-29 | MTEP06 | Vectren - Fred Fredrick |  | Y | N | Y
1971 | 2006-06-29 | BR | E-IOK | Vectren | 1257 | 2006-06-29 | 8.3 | 2011-05-31 | AB Brown 345/138 kV | transformer | 1 | 345 | 138 | 448/470 | New 345 bus & transformer | L11 | IN |  |  |  |  | 50 | 50 | Planned | 8400000 | Budgetary |  |  |  | 2006-06-29 | MTEP06 | Vectren - Fred Fredrick |  | Y | N | Y
1972 | 2006-06-29 | BR | E-IOK | Vectren | 1257 | 2006-06-29 | 8.1 8.2 | 2011-05-31 | AB Brown | Gibson (Duke) | 15 | 345 |  | 1430/1430 | new line | L11 | IN |  | 40 |  |  | 50 | 50 | Planned | 38625000 | Budgetary | 73075000 |  |  | 2006-06-29 | MTEP06 | Vectren - Fred Fredrick |  | Y | N | Y
1931 | 2006-03-16 | Tap | East | WPSC | 1231 | 2006-03-16 | 2006-07 | 2006-06-01 | Superior | New Load |  | 69 |  |  | Add new load tap off 69KV line |  | MI |  |  | 100 |  |  |  | Planned | 550000 | Planning | [7 empty] | Y | N | Y
1900 | 2006-02-10 | CB | E-MIO | WPSC | 1205 | 2006-02-10 | 2006-01 | 2006-08-01 | Cheboygan II | Breaker |  | 69 |  |  | Add Breaker at Cheboygan II |  | MI |  |  | 100 |  |  |  | Planned | 550000 | Planning | [7 empty] | Y | N | Y
1901 | 2006-02-10 | BR | E-MIO | WPSC | 1206 | 2006-02-10 | 2006-02 | 2006-08-01 | Lake County | Bass Lake |  | 69 |  | 102.4 MVA | Rebuild Overloaded Line |  | MI | 8.35 |  | 100 |  |  |  | Planned | 1800000 | Planning | [7 empty] | Y | N | Y
1902 | 2006-02-10 | BR | E-MIO | WPSC | 1207 | 2006-02-10 | 2006-03 | 2006-08-01 | Hersey | Osceola |  | 69 |  | 35.9 MVA | Rerate Overloaded Line |  | MI | 4.02 |  | 100 |  |  |  | Planned | 200000 | Planning | [7 empty] | Y | N | Y
1903 | 2006-02-10 | DV | E-MIO | WPSC | 1208 | 2006-02-10 | 2006-04 | 2006-08-01 | Oden | 12MVAR cap. Bank |  | 69 |  |  | Add 12MVAR at Oden Sub. |  | MI |  |  | 100 |  |  |  | Planned | 300000 | Planning | [7 empty] | Y | N | Y
1930 | 2006-03-16 | Bus | East | WPSC | 1230 | 2006-03-16 | 2006-06 | 2006-09-01 | White Cloud | Bus Upgrade |  | 69 |  |  | Upgrade exsisting 69KV bus |  | MI |  |  | 100 |  |  |  | Planned | 625000 | Planning | [7 empty] | Y | N | Y
1929 | 2006-03-16 | Bus | East | WPSC | 1229 | 2006-03-16 | 2006-05 | 2006-11-01 | Plains X | Bus Upgrade |  | 69 |  |  | Upgrade exsisting 69KV bus |  | MI |  |  | 100 |  |  |  | Planned | 625000 | Planning | [7 empty] | Y | N | Y
1904 | 2006-02-10 | Bus | E-MIO | WPSC | 1209 | 2006-02-10 | 2007-01 | 2007-08-01 | Hersey | Bus Upgrade |  | 69 |  |  | Convert Single Bus to Ring Bus |  | MI |  |  | 100 |  |  |  | Proposed | 2300000 | Planning | [7 empty] | Y | N | Y
1905 | 2006-02-10 | CB | E-MIO | WPSC | 1210 | 2006-02-10 | 2007-02 | 2007-08-01 | Lewiston | Breaker |  | 69 |  |  | Add Breaker at Lewistion |  | MI |  |  | 100 |  |  |  | Proposed | 520000 | Planning | [7 empty] | Y | N | Y
1906 | 2006-02-10 | BR | E-MIO | WPSC | 1211 | 2006-02-10 | 2007-03 | 2007-08-01 | Grand Traverse | Grawn |  | 69 |  | 102.4 MVA | Rebuild Overloaded Line |  | MI | 5.21 |  | 100 |  |  |  | Proposed | 1200000 | Planning | [7 empty] | Y | N | Y
1907 | 2006-02-10 | BR | E-MIO | WPSC | 1212 | 2006-02-10 | 2007-04 | 2007-08-01 | Alpine | Gaylord |  | 69 |  | 41.2 MVA | Rerate Overloaded Line |  | MI | 3.41 |  | 100 |  |  |  | Proposed | 400000 | Planning | [7 empty] | Y | N | Y
1908 | 2006-02-10 | DV | E-MIO | WPSC | 1213 | 2006-02-10 | 2007-05 | 2007-08-01 | Vestaburg | 6MVAR cap. Bank |  | 69 |  |  | Add 6MVAR at Vestaburg Sub. |  | MI |  |  | 100 |  |  |  | Proposed | 3000 | Planning | [7 empty] | Y | N | Y
1995 | 2006-07-27 | BR | East | WPSC | 1273 | 2006-07-27 | 2007-09 | 2007-10-01 | Alpine | Elmira |  | 69 |  | 43.4/56.4MVA | Rerate overloaded line |  | MI | 3.61 |  | 100 |  |  |  | Proposed | 200000 | Planning |  |  |  | 2006-07-27 |  |  |  | Y | N | Y
1996 | 2006-07-27 | BR | East | WPSC | 1274 | 2006-07-27 | 2007-10 | 2007-10-01 | Allendale | Blendon |  | 69 |  | 63.2/82.2MVA | Rerate overloaded line |  | MI | 2.11 |  | 100 |  |  |  | Proposed | 150000 | Planning |  |  |  | 2006-07-27 |  |  |  | Y | N | Y
1997 | 2006-07-27 | BR | East | WPSC | 1275 | 2006-07-27 | 2007-11 | 2007-10-01 | Boyne City | Wilson |  | 69 |  | 43.4/56.4MVA | Rerate overloaded line |  | MI | 3.04 |  | 100 |  |  |  | Proposed | 200000 | Planning |  |  |  | 2006-07-27 |  |  |  | Y | N | Y
1926 | 2006-03-15 | BR | East | WPSC | 1226 | 2006-03-15 | TL06-01 | 2008-02-01 | Kalkaska Generation | Westwood | 1 | 69 |  | 102.4 | Rebuild 69 kV Line |  | MI | 11.62 | 0 | 100 | 0 | 0 | 0 | Planned | 2905000 | Planning |  |  | Two branches in model | 2006-02-07 | MTEP06 |  | ANR El Paso 06 Summer | Y | N | Y
1927 | 2006-03-15 | BR | East | WPSC | 1227 | 2006-03-15 | TL06-02 | 2008-02-01 | Gaylord Generation | Bagley Junction | 1 | 69 |  | 102.4 | Rebuild 69 kV Line |  | MI | 4 | 0 | 100 | 0 | 0 | 0 | Planned | 1000000 | Planning |  |  |  | 2006-02-07 | MTEP06 |  | ANR El Paso 06 Summer | Y | N | Y
1909 | 2006-02-10 | BR | E-MIO | WPSC | 1214 | 2006-02-10 | 2008-01 | 2008-08-01 | Garfield | Grawn |  | 69 |  | 102.4 MVA | Rebuild Overloaded Line |  | MI | 7.68 |  | 100 |  |  |  | Proposed | 1700000 | Planning | [7 empty] | Y | N | Y
1910 | 2006-02-10 | BR | E-MIO | WPSC | 1215 | 2006-02-10 | 2008-02 | 2008-08-01 | Advance | Wilson |  | 69 |  | 41.2 MVA | Rerate Overloaded Line |  | MI | 4.7 |  | 100 |  |  |  | Proposed | 200000 | Planning | [7 empty] | Y | N | Y
1911 | 2006-02-10 | BR | E-MIO | WPSC | 1216 | 2006-02-10 | 2008-03 | 2008-08-01 | Garfield | Hall Street |  | 69 |  | 41.2 MVA | Rerate Overloaded Line |  | MI | 3.72 |  | 100 |  |  |  | Proposed | 150000 | Planning | [7 empty] | Y | N | Y
1912 | 2006-02-10 | Bus | E-MIO | WPSC | 1217 | 2006-02-10 | 2008-04 | 2008-08-01 | Grawn | Bus Upgrade |  | 69 |  |  | Convert Single Bus to Ring Bus |  | MI |  |  | 100 |  |  |  | Proposed | 1900000 | Planning | [7 empty] | Y | N | Y
1928 | 2006-03-16 | Tap | East | WPSC | 1228 | 2006-03-16 | 2008-05 | 2008-08-01 | Westwood | New Load |  | 69 |  |  | Add 14MW Load to Westwood |  | MI |  |  | 100 |  |  |  | Planned | 1800000 | Planning | [7 empty] | Y | N | Y
1913 | 2006-02-10 | Bus | E-MIO | WPSC | 1218 | 2006-02-10 | 2009-01 | 2009-08-01 | Atlanta | Bus Upgrade |  | 69 |  |  | Convert Single Bus to Ring Bus |  | MI |  |  | 100 |  |  |  | Proposed | 1900000 | Planning | [7 empty] | Y | N | Y
1914 | 2006-02-10 | BR | E-MIO | WPSC | 1219 | 2006-02-10 | 2009-02 | 2009-08-01 | Lake County | Star Lake |  | 69 |  | 102.4 MVA | Rebuild Overloaded Line |  | MI | 7.72 |  | 100 |  |  |  | Proposed | 1800000 | Planning | [7 empty] | Y | N | Y
1915 | 2006-02-10 | BR | E-MIO | WPSC | 1220 | 2006-02-10 | 2009-03 | 2009-08-01 | Copemish | Bass Lake |  | 69 |  | 41.2 MVA | Rerate Overloaded Line |  | MI | 28.92 |  | 100 |  |  |  | Proposed | 1200000 | Planning | [7 empty] | Y | N | Y
1916 | 2006-02-10 | BR | E-MIO | WPSC | 1221 | 2006-02-10 | 2010-01 | 2010-08-01 | Redwood | New Era |  | 69 |  | 102.4MVA | Rebuild Overloaded Line |  | MI | 7.54 |  | 100 |  |  |  | Proposed | 1500000 | Planning | [7 empty] | Y | N | Y
1917 | 2006-02-10 | Bus | E-MIO | WPSC | 1222 | 2006-02-10 | 2010-02 | 2010-08-01 | Lake County | Bus Upgrade |  | 69 |  |  | Convert Single Bus to Ring Bus |  | MI |  |  | 100 |  |  |  | Proposed | 3800000 | Planning | [7 empty] | Y | N | Y
1994 | 2006-07-13 | BR | East | WPSC | 1272 | 2006-07-13 | 2010-03 | 2010-08-01 | Redwood 138 | Redwood 69 |  | 138 | 69 | 75MVA | Add 75MV transformer |  | MI | 0 |  | 100 |  |  |  | Planned | 1900000 | Planning |  |  |  | 2006-07-13 |  |  |  | Y | N | Y
1998 | 2006-07-27 | BR | East | WPSC | 1276 | 2006-07-27 | 2010-04 | 2010-10-01 | Burnips | Goodwin |  | 69 |  | 43.4/56.4MVA | Rerate overloaded line |  | MI | 13.09 |  | 100 |  |  |  | Proposed | 900000 | Planning |  |  |  | 2006-07-27 |  |  |  | Y | N | Y
1999 | 2006-07-27 | BR | East | WPSC | 1277 | 2006-07-27 | 2011-01 | 2011-10-01 | Wayland | Goodwin |  | 69 |  | 43.4/56.4MVA | Rerate overloaded line |  | MI | 4.58 |  | 100 |  |  |  | Proposed | 350000 | Planning |  |  |  | 2006-07-27 |  |  |  | Y | N | Y
1777 | 2005-11-18 | GEN | West | XEL | 1127 | 2005-11-18 |  | 2002-09-01 | Garwin McNeilus | generator | 3 | 69 |  | 63 | new generator |  | MN |  |  |  | 100 |  |  | Planned | [8 empty] | G239 | Y | N | Y |  | Generator
1768 | 2005-11-18 | GEN | West | XEL | 1118 | 2005-11-18 |  | 2004-04-01 | Faribault Energy Center | generator | 1 |  |  | 300 | new generator |  | MN |  |  |  | 100 |  |  | Under Construction | [8 empty] | G173 | Y | N | Y |  | Generator
803 | 2004-12-23 | BR | N-NM | XEL | 1031 | 2004-12-23 |  | 2005-03-01 | Kasson | Dodge Center | 1 | 69 |  | 84 | upgrade line | I6 | MN | 7.8 |  |  |  | 100 |  | Planned | 780000 | Planning MISO |  |  | Customer related delay |  |  |  | G239 | Y | Y | Y |  | Network | Y
1763 | 2005-11-18 | GEN | West | XEL | 1113 | 2005-11-18 |  | 2006-05-01 | Fenton PP | generator | 1 |  |  | 200 | new generator |  | MN |  |  |  | 100 |  |  | Planned | [8 empty] | G162 | Y | N | Y |  | Generator
1079 | 2005-09-01 | BR | N-NM | XEL | 1034 | 2005-09-01 |  | 2006-06-01 | Loon Lake 115-69 kV | transformer | 1 | 115 | 69 | 112 |  | H6 | MN |  |  |  | 100 |  |  | Proposed | 1774000 | Planning MISO | [6 empty] | G141 | Y | Y | Y |  | Interconnection
1770 | 2005-11-18 | GEN | West | XEL | 1120 | 2005-11-18 |  | 2006-06-30 |  | generator | 1 |  |  | 4 | new generator |  | MN |  |  |  | 100 |  |  | Planned | [8 empty] | G185 | Y | N | Y |  | Generator
561 | 2006-07-12 | BR | N-NM | XEL | 265 | 2006-07-12 |  | 2006-07-31 | Glencoe | McLeod | 1 | 115 |  | 300 | New line | H6 | MN |  | 9.5 | 100 |  |  |  | Planned | 4282860 |  | 6836860 |  | Customer developed alternate source. |  |  | XEL - Walt Grivna |  | Y | Y | Y
268 | 2006-07-12 | BR | N-NM | XEL | 377 | 2006-07-12 | Wind 425 | 2007-01-01 | Minn Valley | Redwood Falls Tap | 1 | 115 |  | 310 | Upgrade existing 115 kV line | G6 | MN | 27.2 |  |  | 100 |  |  | Planned | 9380127.53 |  |  |  | Project delayed due to conflicting outage requirements with other trransmission projects. This project did not impact reliability so was chosen to be deferred.. |  |  | XEL - Walt Grivna | A046, A053, A055, A058, A059, A102 | Y | Y | Y |  |  | Y
563 | 2006-07-12 | BR | N-NM | XEL | 267 | 2006-07-12 |  | 2007-05-01 | Lawrence | Minnehaha | 1 | 115 |  | 310 | Upgrade existing line | G7 | SD | 5.2 |  | 100 |  |  |  | Planned | 829667 |  |  |  | Load has not developed as fast as expected |  |  | XEL - Walt Grivna |  | Y | Y | Y
564 | 2006-07-12 | BR | N-NM | XEL | 268 | 2006-07-12 |  | 2007-05-01 | Minnehaha | Lincoln County | 1 | 115 |  | 310 | Upgrade existing line | G7 | SD | 5.8 |  | 100 |  |  |  | Planned | 925398 |  |  |  | Load has not developed as fast as expected |  |  | XEL - Walt Grivna |  | Y | Y | Y
1788 | 2005-11-18 | GEN | West | XEL | 1138 | 2005-11-18 |  | 2007-05-01 | Mankato Energy Center | generator |  |  |  | 667 | new generator |  | MN |  |  |  | 100 |  |  | Planned | [8 empty] | G261 | Y | N | Y |  | Generator
1137 | 2006-07-12 | BR | N-NM | XEL | 269 | 2006-07-12 |  | 2007-06-01 | Prairie Island | Red Rock | 2 | 345 |  | 1198 | Upgrade existing line | Q6 | MN | 32 |  | 100 |  |  |  | Planned | 807000 |  |  |  | Capacity raised to 691 sufficient for meeting 2006 requirements remainder of upgrade to be in service 6-1-07 |  |  | XEL - Walt Grivna |  | Y | Y | Y
1138 | 2006-07-12 | BR | N-NM | XEL | 270 | 2006-07-12 |  | 2007-06-01 | Champlin | Champlin Tap | 1 | 115 |  | 310 | Upgrade existing line | O4 | MN | 2.4 |  | 100 |  |  |  | Planned | 382923 |  |  |  | Load has not developed as fast as expected |  |  | XEL - Walt Grivna |  | Y | Y | Y
277 | 2005-07-19 | BR | N-NM | XEL | 272 | 2006-03-27 |  | 2007-06-01 | Air Lake | Vermillion River | 1 | 115 |  | 200 | New line | TC detail | MN |  | 4.2 | 100 |  |  |  | Planned | 3359095.21 | [7 empty] | HBR RIV | Y | Y | Y |  | Net?
573 | 2006-03-27 | BR | N-NM | XEL | 366 | 2006-03-27 | St Cloud | 2007-06-01 | Sherco 345-115 kV | transformer | 1 | 345 | 115 | 448 | New transformer | H5 | MN |  |  | 100 |  |  |  | Planned | 3001443 |  |  |  | based on risk/consequence, project in-service date shifted to NSP project portfolio workflow |  |  | XEL - Jason Standing |  | Y | Y | Y
569 | 2006-03-27 | BR | N-NM | XEL | 366 | 2006-03-27 | St Cloud | 2007-06-01 | I94 Industrial Park tap | Salida Crossing | 1 | 115 |  | 310 | Upgrade existing line | H5 | MN | 14.3 |  | 100 |  |  |  | Planned | 2432170 |  |  |  | based on risk/consequence, project in-service date shifted to NSP project portfolio workflow |  |  | XEL - Jason Standing |  | Y | Y | Y
571 | 2006-03-27 | BR | N-NM | XEL | 366 | 2006-03-27 | St Cloud | 2007-06-01 | Salida Crossing | Sherco | 1 | 115 |  | 310 | Upgrade existing line | H5 | MN | 2.5 | 1 | 100 |  |  |  | Planned | 765368 |  |  |  | based on risk/consequence, project in-service date shifted to NSP project portfolio workflow |  |  | XEL - Jason Standing |  | Y | Y | Y
572 | 2006-03-27 | BR | N-NM | XEL | 366 | 2006-03-27 | St Cloud | 2007-06-01 | Sherco | Monticello | 1 | 115 |  | 310 | Upgrade existing line | H5 | MN | 2.2 | 1 | 100 |  |  |  | Planned | 714344 |  |  |  | based on risk/consequence, project in-service date shifted to NSP project portfolio workflow |  |  | XEL - Jason Standing |  | Y | Y | Y
574 | 2006-03-27 | BR | N-NM | XEL | 366 | 2006-03-27 | St Cloud | 2007-06-01 | St Cloud | I94 Industrial Park tap | 1 | 115 |  | 310 | Upgrade existing line | H5 | MN | 5 |  | 100 |  |  |  | Planned | 850409 |  |  |  | based on risk/consequence, project in-service date shifted to NSP project portfolio workflow |  |  | XEL - Jason Standing |  | Y | Y | Y
2038 | 2006-07-12 | DV | N-NM | XEL | 417 | 2006-07-12 |  | 2007-06-01 | Westgate | Capacitor |  | 115 |  | 80 Mvar | New capacitor | Twin City | MN |  |  | 100 |  |  |  | Planned | 1500000 |  |  |  | Under Construction. This project is expected to be completed by mid 2007. |  |  | XEL - Walt Grivna |  | Y | Y | Y
800 | 2006-07-12 | BR | N-NM | XEL | 609 | 2006-07-12 |  | 2007-06-01 | Long Lake | Oakdale (from Woodbury) | 1 | 115 |  | 310 | Upgrade existing line | P5 | MN | 3.7 |  | 100 |  |  |  | Planned | 760000 |  |  |  | Due to the slower than expected load growth in this area this upgrade is delayed |  |  | XEL - Walt Grivna |  | Y | Y | Y
1359 | 2006-07-12 | BR | N-NM | XEL | 671 | 2006-07-12 |  | 2007-06-01 | Oakdale | Tanners Lake | 1 | 115 |  | 223 | Upgrade existing line | P5 | MN | 5.2 |  | 100 |  |  |  | Planned | 800000 |  |  |  | Due to the slower than expected load growth in this area this upgrade is delayed |  |  | XEL - Walt Grivna |  | Y | Y | Y
3020 | 2005-07-19 | DV | N-NM | XEL | 752 | 2005-07-19 |  | 2007-06-01 | Edgewater | Capacitor |  | 69 |  | 5.4 Mvar | New capacitor | I5 | WI |  |  | 100 |  |  |  | Proposed | 412000 | Planning MISO | [7 empty] | Y | Y | Y
975 | 2005-07-19 | BR | N-NM | XEL | 385 | 2005-07-19 | Wind 825 | 2007-07-01 | Nobles Co 345-115 kV | transformer | 2 | 345 | 115 | 600 | New transformer | G7 | MN |  |  |  | 100 |  |  | Planned | 5792804.9564 | [7 empty] | A053, A055, A058, A059 | Y | Y | Y |  |  | Y
307 | 2006-03-27 | BR | N-NM | XEL | 385 | 2005-07-19 | Wind 825 | 2007-10-01 | Nobles Co | Lakefield Jct | 1 | 345 |  | 2085 | New line | G7 | MN |  | 42 |  | 100 |  |  | Planned | 37070397.4058 |  |  |  | Actual need for project is October 2007. ISD is proposed construction schedule that will move around for sequencing purposes |  |  | XEL - Jason Standing | A053, A055, A058, A059, A102 | Y | Y | Y |  |  | Y
309 | 2006-03-27 | BR | N-NM | XEL | 385 | 2005-07-19 | Wind 825 | 2007-10-01 | Nobles Co 345-115 kV | transformer | 1 | 345 | 115 | 600 | New transformer | G7 | MN |  |  |  | 100 |  |  | Planned | 5792804.9564 |  |  |  | Actual need for project is October 2007. ISD is proposed construction schedule that will move around for sequencing purposes |  |  | XEL - Jason Standing | A053, A055, A058, A059, A102 | Y | Y | Y |  |  | Y
308 | 2006-03-27 | BR | N-NM | XEL | 385 | 2005-07-19 | Wind 825 | 2007-10-01 | Nobles Co | Fenton | 1 | 115 |  | 600 | New line | G7 | MN |  | 12 |  | 100 |  |  | Planned | 7913905.0642 |  |  |  | Actual need for project is October 2007. ISD is proposed construction schedule that will move around for sequencing purposes |  |  | XEL - Jason Standing | G162, A053, A055, A058, A059, A102 | Y | Y | Y |  | Network | Y
272 | 2006-03-27 | BR | N-NM | XEL | 385 | 2005-07-19 | Wind 825 | 2007-10-01 | Redwood Falls Tap | Franklin | 1 | 115 |  | 310 | Upgrade existing 115 kV line | H6 | MN | 13 |  |  | 100 |  |  | Planned | 3185000 |  |  |  | Actual need for project is October 2007. ISD is proposed construction schedule that will move around for sequencing purposes |  |  | XEL - Jason Standing | A053, A055, A058, A059, A102 | Y | Y | Y |  |  | Y
302 | 2006-03-27 | BR | N-NM | XEL | 385 | 2005-07-19 | Wind 825 | 2007-11-01 | Fenton | Chanarambie | 1 | 115 |  | 600 | New 115 kV line | G6 | MN |  | 14 |  | 100 |  |  | Planned | 7412392.6347 |  |  |  | Actual need for project is November 2007. ISD is proposed construction schedule that will move around for sequencing purposes |  |  | XEL - Jason Standing | G162, A053, A055, A058, A059, A102 | Y | Y | Y |  | Network | Y
311 | 2006-03-27 | BR | N-NM | XEL | 385 | 2005-07-19 | Wind 825 | 2007-11-01 | Split Rock | Nobles Co | 1 | 345 |  | 2085 | New line | G7 | MN |  | 52 |  | 100 |  |  | Planned | 44966947.415 |  |  |  | Actual need for project is November 2007. ISD is proposed construction schedule that will move around for sequencing purposes |  |  | XEL - Jason Standing | A053, A055, A058, A059, A102 | Y | Y | Y |  |  | Y
537 | 2006-03-27 | BR | N-MB | XEL | 385 | 2005-07-19 | Wind 825 | 2007-11-01 | Buffalo Ridge | Brookings Co (was White) | 1 | 115 |  | 310 | New line | G6 | MN |  | 26 |  | 100 |  |  | Planned | 9575000 |  |  |  | Change in project. Terminated at Brookings Co near White |  |  | XEL - Jason Standing | A053, A055, A058, A059, A102 | Y | Y | Y |  |  | Y
2041 | 2005-11-28 | DV | N-NM | XEL | 385 | 2005-07-19 | Wind 825 | 2007-11-01 | Nobles Co | Capacitor |  | 115 |  | 40 Mvar | New capacitor | G7 | MN |  |  |  | 100 |  |  | Planned | 634038.2211 |  |  |  | Actual need for project is December 2007. ISD is proposed construction schedule that will move around for sequencing purposes |  |  |  | A053, A055, A058, A059, A102 | Y | Y | Y |  |  | Y
3086 | 2006-07-12 | DV | N-NM | XEL | 778 | 2006-07-12 | Wind825 | 2007-11-01 | Nobles Co | Reactor #2 |  | 34.5 |  | 50 Mvar | New reactor | G7 | MN |  |  |  | 100 |  |  | Planned | 200000 |  |  |  | Actual need for project is December 2007. ISD is proposed construction schedule that will move around for sequencing purposes |  |  | XEL - Walt Grivna | Gen | Y | Y | Y
3088 | 2006-07-12 | DV | N-NM | XEL | 780 | 2006-07-12 | Wind 825 | 2007-11-01 | Fieldon Township | Series Capacitor |  | 345 |  | 20 ohms | New series capacitor on LGS-Wilmarth 345 | H6 | MN |  |  |  | 100 |  |  | Planned | 10100000 |  |  |  | Actual need for project is November 2007. ISD is proposed construction schedule that will move around for sequencing purposes |  |  | XEL - Walt Grivna | A046, A053, A055, A058, A059, A102 | Y | Y | Y |  |  | Y
3019 | 2005-07-19 | DV | N-NM | XEL | 751 | 2005-07-19 |  | 2007-12-01 | Nobles Co | Reactor #1 |  | 34.5 |  | -50 Mvar | New reactor | G7 | MN |  |  |  | 100 |  |  | Proposed | 200000 | Planning MISO | [7 empty] | Y | Y | Y
1088 | 2004-12-23 | BR | N-NM | XEL | 56 | 2006-03-27 |  | 2007-12-31 | Lawrence Creek 115-69 kV | transformer | 1 | 115 | 69 | 70 |  | I5 | MN |  |  | 100 |  |  |  | Planned | 1631000 | Planning MISO | 161394235.3936 | [6 empty] | Y | Y | Y
1767 | 2005-11-18 | GEN | West | XEL | 1117 | 2005-11-18 |  | 2008-01-01 |  | generator | 1 |  |  | 20 | new generator |  | MN |  |  |  | 100 |  |  | Planned | [8 empty] | G170 | Y | N | Y |  | Generator
1362 | 2006-07-12 | BR | N-NM | XEL | 674 | 2006-07-12 |  | 2008-05-01 | High Bridge | Rogers Lake | 1 | 115 |  | 585 | Upgrade existing line | TC detail | MN | 4.2 |  |  | 100 |  |  | Planned | 2400000 |  |  |  | This project is required for the new High Bridge generation addition, as the new generators are expected to be online in 2008, there is no negative impact on the system. |  |  | XEL - Walt Grivna | G043, G237 | Y | Y | Y |  | Network
1795 | 2005-11-18 | GEN | West | XEL | 1145 | 2005-11-18 |  | 2008-05-01 | High Bridge MERP | generator | P1 |  |  | 575 | new generator |  | MN |  |  |  | 100 |  |  | Planned | [8 empty] | G237 | Y | N | Y |  | Generator
1361 | 2006-07-12 | BR | N-NM | XEL | 673 | 2006-07-12 |  | 2008-06-01 | Champlin Tap | Crooked Lake | 1 | 115 |  | 223 | Upgrade existing line | TC detail | MN | 3.1 |  | 100 |  |  |  | Planned | 2 |  |  |  | Due to the slower than expected load growth in this area this upgrade is delayed |  |  | XEL - Walt Grivna |  | Y | Y | Y
565 | 2006-07-12 | BR | N-NM | XEL | 271 | 2006-07-12 |  | 2008-09-01 | Hungry Hollow | Ballard Corner | 1 | 115 |  |  | Upgrade 69 kV to 115 kV | H6 | MN |  |  | 100 |  |  |  | Planned | 1333975 |  | 17733977 |  | This project will be done in 2008 along with GRE's hungry Hollow switching station. Project is for a power quality, not reliability issue at this time. |  |  | XEL - Walt Grivna |  | Y | Y | Y
1364 | 2006-07-12 | BR | N-NM | XEL | 675 | 2006-07-12 |  | 2009-06-01 | Westgate | Scott County | 1 | 115 |  | 310 | Upgrade 69 kV to 115 kV | TC detail | MN | 20.1 |  | 100 |  |  |  | Proposed | 14000000 |  | Advanced to 2009 |  |  |  |  | XEL - Walt Grivna | 2003 Glen Lake area transmission study | Y | Y | Y
306 | 2006-03-27 | BR | N-NM | XEL | 56 | 2006-03-27 | 41 | 2010-12-31 | Lindstrom | Shafer | 1 | 115 |  | 310 | New line | Q4 | MN | 2.8 |  | 100 |  |  |  | Planned | 5800000 |  |  |  | Need to file a certificate of Need with state of Minnesota |  |  | XEL - Jason Standing |  | Y | Y | Y
303 | 2006-03-27 | BR | N-NM | XEL | 56 | 2006-03-27 | 41 | 2010-12-31 | Lawrence Creek | St Croix Falls | 1 | 161 |  | 371 | New 161 kV line | Q4 | MN |  | 2.05 | 100 |  |  |  | Planned | 9080000 |  |  |  | Need to file a certificate of Need with state of Minnesota |  |  | XEL - Jason Standing |  | Y | Y | Y
301 | 2006-03-27 | BR | N-NM | XEL | 56 | 2006-03-27 | 41 | 2010-12-31 | Chisago | Lindstrom | 1 | 115 |  | 310 | New 115 kV line | Q4 | MN | 7 |  | 100 |  |  |  | Planned | 10100000 |  |  |  | Need to file a certificate of Need with state of Minnesota |  |  | XEL - Jason Standing |  | Y | Y | Y
310 | 2006-03-27 | BR | N-NM | XEL | 56 | 2006-03-27 | 41 | 2010-12-31 | Shafer | Lawrence Creek | 1 | 115 |  | 310 | New line | Q4 | MN | 6.2 |  | 100 |  |  |  | Planned | 3500000 |  |  |  | Need to file a certificate of Need with state of Minnesota |  |  | XEL - Jason Standing |  | Y | Y | Y
304 | 2006-03-27 | BR | N-NM | XEL | 56 | 2006-03-27 | 41 | 2010-12-31 | Lawrence Creek 161-115 kV | transformer | 1 | 161 | 115 | 336 | New substation with 161-115 kV transformer | Q4 | MN |  |  | 100 |  |  |  | Planned | 6000000 |  | 34480000 |  | Need to file a certificate of Need with state of Minnesota |  |  | XEL - Jason Standing |  | Y | Y | Y
1870 | 2005-12-05 | DV | West | XEL |  |  |  |  | Maynard | Capacitor |  | 115 |  | 40 Mvar | New Capacitor |  | MN |  |  |  |  | 100 |  | Planned |  |  |  |  | Submitted by MISO |  |  |  | A046, A053, A055, A058, A059, A102 | Y | N | Y |  |  | Y
1871 | 2005-12-05 | BR | West | XEL |  |  |  |  | Panther | ??? |  | 230 |  |  | Panther 230 kV line termination uprate (DKD thought it was GFA termination) |  | MN |  |  |  |  | 100 |  | Planned |  |  |  |  | Submitted by MISO |  |  |  | A046, A053, A055, A058, A059, A102 | Y | N | Y |  |  | Y
1872 | 2005-12-05 | DV | West | XEL |  |  |  |  | Split Rock | Capacitor |  |  |  | 50 Mvar | New Capacitor (is this reactor?) |  | SD |  |  |  |  | 100 |  | Planned |  |  |  |  | Submitted by MISO |  |  |  | A046, A053, A055, A058, A059, A102 | Y | N | Y |  |  | Y
266 | 2006-07-12 | BR | N-NM | XEL/ALT | 377 | 2006-07-12 | Wind 425 | 2006-11-01 | Lakefield Jct | Fox Lake | 2 | 161 |  | 434 | new line | G7 | MN |  | 24 |  | 100 |  |  | Planned | 6000000 |  |  |  | Complexity of study work associated with final substation designs delayed the project. |  |  | XEL - Walt Grivna | A053, A055, A058, A059, A102 | Y | Y | Y |  |  | Y
1669 | 2005-10-12 | BR | N-NM | XEL/DPC | 1024 | 2005-10-12 | SE MN - SW WI | 2011-12-31 | North La Crosse | North La Crosse Tap | 1 | 161 |  | 304 |  | J6 | WI | 0.5 | 0.5 | 100 |  |  |  | Proposed | 400000 | MISO planning |  |  | upgrade DPC, new XEL | 2005-10-12 |  |  | SE MN - SW WI | Y | Y | Y
1670 | 2005-10-12 | BR | N-NM | XEL/DPC | 1024 | 2005-10-12 | SE MN - SW WI | 2011-12-31 | North La Crosse | North La Crosse Tap | 2 | 161 |  | 304 |  | J6 |  | 0.5 | 0.5 | 100 |  |  |  | Proposed | 400000 | MISO planning |  |  | upgrade DPC, new XEL | 2005-10-12 |  |  | SE MN - SW WI | Y | Y | Y
1675 | 2005-10-12 | BR | N-NM | XEL/DPC/RPU | 1024 | 2005-10-12 | CAPX Group 1 | 2011-12-31 | North Rocheter |  | 1 | 345 | 161 | 448 | new transformer | I6 |  |  |  | 100 |  |  |  | Proposed | 9000000 | MISO planning |  |  |  | 2005-10-12 |  |  | SE MN - SW WI | Y | Y | Y
1676 | 2005-10-12 | BR | N-NM | XEL/DPC/RPU | 1024 | 2005-10-12 | CAPX Group 1 | 2011-12-31 | North La Crosse |  | 1 | 345 | 161 | 448 | new transformer | J6 |  |  |  | 100 |  |  |  | Proposed | 9000000 | MISO planning |  |  |  | 2005-10-12 |  |  | SE MN - SW WI | Y | Y | Y
1674 | 2005-10-12 | BR | N-NM | XEL/DPC/RPU | 1024 | 2005-10-12 | CAPX Group 1 | 2011-12-31 | Rochester | North La Crosse | 1 | 345 |  | 1165 | new line | I6 |  |  | 100 | 100 |  |  |  | Proposed | 82000000 | MISO planning |  |  |  | 2005-10-12 |  |  | SE MN - SW WI | Y | Y | Y
1677 | 2005-10-12 | BR | N-NM | XEL/DPC/RPU | 1024 | 2005-10-12 | SE MN - SW WI | 2011-12-31 | North Rochester | Northern Hills | 1 | 161 |  | 302 | new line | I6 |  |  | 2 | 100 |  |  |  | Proposed | 1000000 | MISO planning |  |  |  | 2005-10-12 |  |  | SE MN - SW WI | Y | Y | Y
1678 | 2005-10-12 | BR | N-NM | XEL/DPC/RPU | 1024 | 2005-10-12 | SE MN - SW WI | 2011-12-31 | North Rochester | Chester | 1 | 161 |  | 302 | new line | I6 |  |  | 18 | 100 |  |  |  | Proposed | 9000000 | MISO planning |  |  |  | 2005-10-12 |  |  | SE MN - SW WI | Y | Y | Y
1673 | 2005-10-12 | BR | N-NM | XEL/DPC/RPU | 1024 | 2005-10-12 | CAPX Group 1 | 2011-12-31 | Prairie Island | Rochester | 1 | 345 |  | 1165 | new line | I6 |  |  | 50 | 100 |  |  |  | Proposed | 41000000 | MISO planning | 151800000 |  |  | 2005-10-12 |  |  | SE MN - SW WI | Y | Y | Y
646 | 2006-01-25 | BR | N-NM | XEL/WAPA | 385 | 2005-07-19 | Wind 825 | 2007-11-01 | Brookings Co | 345/115 transformer | 1 | 345 | 115 | 672 |  | G6 | SD |  |  |  |  | 100 |  | Planned | 12179190 |  |  |  | Official planned in-service date for project is October 26 2007. ISD is proposed construction schedule that will move around for sequencing purposes |  |  |  |  | Y | Y | Y
645 | 2006-03-27 | BR | N-NM | XEL/WAPA | 385 | 2005-07-19 | Wind 825 | 2007-11-01 | Brookings Co | White | 1 | 345 |  | 600 |  | G6 | SD |  | 2 |  |  | 100 |  | Planned |  |  |  |  | Miles and cost? Official planned in-service date for project is October 26 2007. ISD is proposed construction schedule that will move around for sequencing purposes |  |  | XEL - Jason Standing |  | Y | Y | Y
1874 | 2005-12-05 | BR | [6 empty] | Cambridge | Princeton |  |  |  |  | Cambridge-Dalbo Tap-Princeton North-Princeton | [6 empty] | 100 |  | Planned |  |  |  |  | Submitted by MISO |  |  |  | A236 | Y | N | Y |  |  | Y
1873 | 2005-12-05 | BR | [6 empty] | Cambridge | Grasston |  |  |  |  | Cambridge-Braham-Grasston | [6 empty] | 100 |  | Planned |  |  |  |  | Submitted by MISO |  |  |  | A236 | Y | N | Y |  |  | Y
1875 | 2005-12-05 | BR | [6 empty] | Cambridge | Athens |  |  |  |  | Cambridge-Industrial Tap-Isanti Tap-Athens | [6 empty] | 100 |  | Planned |  |  |  |  | Submitted by MISO |  |  |  | A236 | Y | N | Y |  |  | Y
1876 | 2005-12-05 | BR | [6 empty] | Cambridge | Rush City |  |  |  |  | Cambridge-Rush Tap-Rush City | [6 empty] | 100 |  | Planned |  |  |  |  | Submitted by MISO |  |  |  | A236 | Y | N | Y |  |  | Y
1877 | 2005-12-05 | DV | [6 empty] | St Germain or Conover | capacitor |  | 115 |  |  | Install at least an 8 MVAR, 115kV Capacitor Bank at the St. Germain substation or an 8 MVAR, 138kV Capacitor Bank at the Conover substation. | [6 empty] | 100 |  | Planned |  |  |  |  | Submitted by MISO |  |  |  | A105, F006 | Y | N | Y |  |  | Y
1879 | 2005-12-05 | BR | [6 empty] | Stoughton | Stoughton Muni |  | 69 |  |  | Stoughton-Stoughton Muni. 69kV line to be retired. | [6 empty] | 100 |  | Planned |  |  |  |  | Submitted by MISO |  |  |  | A120 | Y | N | Y |  |  | Y
1880 | 2005-12-05 | BR | [6 empty] | N. Beaver Dam | Waupin |  | 69 |  | 50 | Uprate of existing line | [6 empty] | 100 |  | Planned |  |  |  |  | Submitted by MISO |  |  |  | A120 | Y | N | Y |  |  | Y
4558410585.983
Includes generator interconnection projects
Includes sub-transmission projects