## Planning
2025-04-01
ISD has passed
ISD is within 90 days of Queue posting
LIRF/DERRF Received | LIRF/DERRF Complete | LIRF/DERRF ID # | Distribution Customer | Project Name | Project Type | Estimated ATC Project Lead-Time After PCA Execution | Requested In-Service Date | Projected Scope of Work | Notes & Updates | ATC Planner | BVP Type
2023-09-13 | 2023-09-27 | 40895 | Alliant Energy | Baraboo | Xfmr Repl | 18 | 2028-06-01 | Alliant to rebuild the existing Baraboo substation in place. The drivers for the rebuild include an older transformer that’s starting to fail and to prepare for a future conversion of the distribution voltage to 24.9kV. Alliant will be providing a portable substation as part of the project. One potential “cost adder” they mentioned was that the city of Baraboo is interested in potentially relocating the substation (see the project notes section for more info). Additional LDC scope if this were to go through includes:Alliant constructing a new substation at the specified site.Alliant to install the distribution equipment at this location instead and retire the existing equipment at the original site. ATC to install new jumpers & insulators to the Alliant transformer. ATC connect/disconnect the portable substation as needed. The ATC scope of work for the substation relocation “cost adder” includes:ATC to replace one existing T-Line structure to re-route the line to the new location.ATC to install two new T-Line structures to re-route the line to the new location.ATC to install necessary conductor (~0.04mi) to re-route to the new location.ATC to install two new dead-end structures inside the substation.ATC to install a new loop through bus (in place of existing box structure).ATC to install new circuit switcher for the shunt capacitor bank at this substation.ATC to install a new 10.4MVAR capacitor bank.ATC to retire 9 existing T-Line structures that would be no longer needed.ATC to retire existing substation equipment at the original substation. | 3/6/25- ISD moves to 6/1/28, Site 2 has been selected. 2/28/24- per QP discussion, ISD moves to 06/01/27 10/27/23- ICC email sent to customer. CW letter to follow. 9/27/23- LIRF deemed complete and customer notified | Mainwaring, Kyle | Alternative Assessment
2024-09-05 | 2024-09-18 | 41033 | Alliant Energy | Blanchardville | Sub Rebuild | 12 | 2030-12-30 | WPL is planning to rebuild the Blanchardville SS ATC scope - Assumed jumpers, insulators and minimal t-line pole replacements. | 3/6/25- ISD moves to 2030 per QP meeting. 10/16/24- initial MCW determination sent to customer, letter to follow 9/18/24- LIRF deemed complete and customer notified | Mainwaring, Kyle | MCW
2019-08-14 | 2019-08-28 | 40578 | Alliant Energy | Bonnie Road | New Sub | 24 | 2028-12-31 | WPL to construct a new Drumlin Substation with one 69/12 kV, 33 MVA transformer. ATC to extend 0.5 mile of 69 kV radial tap off line Y-81 (Sun Prairie – Kegonsa). | 3/6/25- ISD moves to 2028 per QP meeting. 9/27/24- per planning meeting, ISD moves to 12/31/27. WPL to submit revised LIRF. 8/20/24- moved back into planning. Discuss with WPL, is a revised LIRF needed? 2/28/24- per QP discussion, ISD moves to 12/31/26 ​4/5/23- ISD moves to 12/31/25 1/31/22- per Greg A, ISD moves to 12/31/24 7/23/21- PM assigned, customer notified 3/22/21- CW letter executed 3/9/21- per QP meeting, name is updated to Bonnie Road 8/28/19- LIRF deemed complete and customer notified | Mainwaring, Kyle | Alternative Assessment
2025-01-13 | 2025-01-15 | 41079 | Alliant Energy | Cambridge | High Side Protection Replacement | 12 | 2025-12-31 | WPL to replace the 138 kV circuit switcher with a 138 kV GOAB switch and 138 kV 2000A breaker. The 138kV GOAB will be installed on the existing Dead End along with inverted line arresters. The 138kV Breaker will be placed where the old 138kV Circuit Switcher was physically located. There will be no changes to the power transformer or distribution equipment. The time of year will determine whether a portable substation is needed for this project. ATC Scope of Work: New jumpers and insulators Potential connection to a portable substation is needed for this project. | 2/12/15- MCW letter sent to customer 1/15/25- LIRF deemed complete and customer notified | Mainwaring, Kyle | MCW
2017-09-25 | 2017-10-09 | 40483 | Alliant Energy | Edgewater | New Sub | 24 | 2030-12-31 | Edgewater distribution XFMR relocate to new sub location across the street from generation switch yard. Install one XFMR but have space for two. ATC loop-thru 138 kV line X-37 with two line breakers and make space provision for bus-tie breaker. | 1/23/25-move back to Planning queue until guidance from WPL. Revised LIRF or new LIRF to be submitted? 11/30/22- update from Logan B - ISD moves to 12/31/30. Will cancel the current PR for the project and will be re-issued closer to the ISD. 09/15/20- per QP meeting, ISD moves to 2025 10/9/19- per QP meeting, ISD moves to 12/31/22 03/29/19 PM assigned and customer notified 3/7/19- CW letter executed 10/09/17- LIRF deemed complete and customer notified | Brecklin, Logan | Alternative Assessment
2024-04-18 | 2024-05-01 | 40973 | Alliant Energy | Fountain Valley | Xfmr Repl | 12 | 2027-12-31 | WPL to replace the existing transformer (T41) at Fountain Valley with a new 69/12.49kV 10/12.5 MVA unit. WPL to replace their high side protective devices with a new2000A circuit breaker (5003-S) and a visible disconnect switch (5003-L). WPLwill also modernize their system protection and install SCADA for monitoring and control. ATC will provide new jumpers/insulators to support the installationof the new high side disconnect switch (5003-L). ATC will also provide support for the portable sub needed for this project. | 12/20/24- project intake submitted in Exto -PI143 5/29/24- MCW letter sent to customer 5/1/24- LIRF deemed complete and customer notified | Mainwaring, Kyle | MCW
2024-07-23 | 2024-08-05 | 41016 | Alliant Energy | Friendship | Sub Rebuild | 18 | 2026-12-31 | Alliant is planning to relocate their Friendship sub away from the nearby lake due to access issues. They have been working on securing new land, but have not been able to finalize a new location for the substation at this point. ATC scope will be dependent on the new sub location. Ryan informed ATC planning that he will stay in communication regarding the land acquisition progress. | 9/3/24- ICC email sent to customer, ATC scope TBD until location is selected 8/5/24- LIRF deemed complete and customer notified 8/16/22- ISD moves to 6/1/26 1/31/22- per QP meeting, ISD moves to 6/1/25 6/15/21- Added per QP Meeting | Mainwaring, Kyle | Alternative Assessment
2017-07-21 | 2017-08-04 | 40472 | Alliant Energy | Loganville | Xfmr Repl | 12 | 2028-12-31 | Alliant transformer replacement and sub rebuild on existing land. MCW for ATC new jumpers and insulators to accommodate new dead-end and connect portable sub. | 12/20/24- submitted in Exto -PI142 10/15/24- MCW letter sent to customer 8/16/22- ISD moves to 12/31/28 6/15/21- per QP meeting, ISD moves to 12/31/26 1/25/21- Per email from Chris Allen, ISD moves to 2024 6/12/19- ISD moves to 12/31/23 3/13/19- per QP meeting, ISD moves from 2021 to 2022 08/04/17- LIRF deemed complete and customer notified | Mainwaring, Kyle | MCW
2024-09-18 | 2024-09-27 | 41037 | Alliant Energy | Neenah Creek | Retirement | 12 | 2027-12-31 | WPL to retire Neenah Creek SS and all distribution assets. Neenah Creek load will be transferred to Oxford SS and future forecasted under Oxford SS. (LIRF #40658) Retirement of Y-181 tapped line section (NCKT-NCK) serving Neenah Creeks SS, including: Replacement of three-way GOAB with tangent structure. Retirement of jumpers and insulators entering Neenah Creek SS. | 12/20/24- Submitted in Exto in Dec 2024, PI139 10/24/24- MCW letter sent to customer 9/27/24- LIRF deemed complete and customer notified | Mainwaring, Kyle | MCW
2024-09-30 | 2024-10-03 | 41040 | Alliant Energy | Polar (Polar Solar) DER | Distributed Energy Resource | 12 | 2026-06-01 | Third party developer to install a new 3.0 MW and/or a 5.0 MW solar DER facility. WPL to connect the new facility/facilities to the distribution side of the Polar transformer T1. Total DER on T1 > 1/3 minimum load for all scenarios. ATC to upgrade the following surge arresters to 57kV MCOV to support the project: Line Y-123 (Aurora St - Deer Trail) both terminals. Line Y-86 (Deer Trail - Whitcomb) both terminals. | 3/6/25- per update from Bob, only the 3 MW project will proceed, no DER AFS needed 10/31/24- MCW letter sent to customer 10/7/24- Initial MCW determination sent to customer. MCW letter to follow after cross functional review. 10/3/24- DERRF deemed complete and customer notified | Van Gaal, Megan | MCW
2024-08-08 | 2024-08-14 | 41022 | Alliant Energy | Spring Brook | Sub Rebuild | 12 | 2027-12-31 | Alliant is planning to replace their Spring Brook transformer and build a five-circuit overhead distribution bus. They plan to retire their current assets and install the new equipment in the same location as the old equipment. ATC will need to re-jumper to the new transformer in the same location as the existing transformer. | 12/20/24- Submitted in Exto in Dec 2024, PI143 9/13/24- MCW letter sent to customer 08/14/24- LIRF deemed complete and customer notified | Mainwaring, Kyle | MCW
2023-11-03 | 2023-11-17 | 40924 | Alliant Energy | Sunrise | Additional Xfmr | 18 | 2028-12-01 | Alliant submitted this LIRF for a proposed expansion at the Sunrise substation. Alliant plans to install a second transformer (138/24.9kV 20/33MVA) and distribution bus off the future open position at the Sunrise substation.LIRF lists project drivers to be high loading on the existing Sunrise transformer and difficulty bridging the entire peak load when the transformer is out of service. Alliant also plans to upgrade the high side protection on the existing T31 transformer from a circuit switcher to a breaker. LIRF notes ongoing coordination between ATC & WPL for the MISO J1460 solar project at Sunrise.The J1460 solar project involves ATC 138kV bus work and is when the additional 138kV terminal will be added.Alliant plans to complete the installation of the new equipment during or after the J1460 project wraps up.At a minimum Alliant would like to perform the breaker upgrade on the existing equipment and install the high side switch for the new equipment during the J1460 bus work outage. ATC to install new jumpers & insulators to the new Alliant breaker. ATC to install new jumpers & insulators to the new Alliant switch. ATC to consider installing a firewall between the existing ATC control house and the existing WPL transformer #31.When Alliant first floated the project Chris Glauser reached out internally to note the distance between the two pieces of equipment is only ~12’ and could warrant a firewall for protection.As mentioned above, the addition of a 138kV terminal is included in the J1460 scope of work. | 2/26/25- CW letter executed 12/18/23- ICC email sent to customer. CW letter to follow at a later date. 11/17/23- LIRF deemed complete and customer notified | Mainwaring, Kyle | Alternative Assessment
2023-12-19 | 2024-01-16 | 40948 | Alliant Energy | West Towne | High Side Protection Replacement | 18 | 2028-12-31 | Alliant to replace their West Towne substation switchgear. This is being done to prepare for the conversion of the distribution system to 24.9kV (currently 13.1kV). Alliant will also upgrade their high side protection from a circuit switcher to a breaker and disconnect. LIRF notes that due to space constraints, ATC bus modifications will be required to accommodate the new breaker and disconnect. The existing transformer will be kept as part of this project. ATC to perform the connection & disconnection of the portable substation. ATC to rebuild the bus on the Alliant section of the substation. The high and low sections of bus will be swapped so that the “loop through” section is high and the “distribution tap” section is low. It will then match the other two MGE sections upon completion. The “tap section” will be shifted North slightly to better align with the new breaker. Further review should be done on the C-phase angled transition to verify the bus/disconnect clearances are sufficient. ATC to replace the disconnect switches on either side of the bus section being worked on. ATC to relocate the bus PTs to match the “tap section” shift North. ATC to install new jumpers & insulators to the new Alliant disconnect switch. ATC to consider repairing/replacing the bus foundations as the LIRF notes there is some deterioration going on. ATC to consider performing a LiDAR scan of the substation to verify drawing dimensions are accurate given the tighter clearances. | 9/19/24- revised ISD provided by Greg A via email 2/28/24- per QP discussion, ISD moves to 12/31/27 2/15/24- Initial CW determination email sent to customer. CW letter to follow. 1/16/2024- LIRF deemed complete and customer notified | Mainwaring, Kyle | Alternative Assessment
2024-06-13 | 2024-06-26 | 40996 | BPMA | East Shawano | Xfmr Repl | 18 | 2027-11-01 | BPMA to install a new second transformer at East Shawano 69kV substation Bus 5. The new transformer will have the same MVA rating as the existing one (25/33.3/41.7 MVA 55-degree rise and 28/36.7/46.7 MVA 65-degree rise) BPMA to keep the existing transformer as an energized reserve without any load. ATC to install a second bus tie disconnect switch between Bus 4 and Bus 5 with space provision for a circuit breaker. ATC to install new jumpers and insulators to BPMA high side disconnect for the new transformer. ATC to perform necessary protection modifications to support an additional distribution transformer. | 3/25/25 - ISD updated via Forster meeting 8/9/24- MCW letter sent to customer 6/26/24- LIRF complete and customer notified | Mainwaring, Kyle | MCW
2024-11-26 | 2024-12-04 | 41059 | Central Wisconsin Electric Cooperative | Central | New Sub | 24 | 2026-04-01 | Central Wisconsin Electric Cooperative will install a new 69 kV to 7.2/12.47 kV substation. The anticipated site is on CWEC property just off Lystul Road which would be approximately 0.3 miles from an existing ATC 69 kV transmission line.. ATC Scope of Work: Install 3-way GOAB switch structure with whips near Y-71 structure 99. Route approx. 0.5 miles of new 69kV line to new SS location. | 3/17/25 - moved to SRA program, PM to be assigned. Kaylin to send email to customer once PM available. 2/13/25- CW letter executed Entered into Exto - PI148 2/7/25- CW letter sent to CWEC for execution 1/3/25- ICC email sent to customer, CW letter to follow. 12/4/24- LIRF deemed complete and customer notified | Mainwaring, Kyle | Alternative Assessment
2025-02-20 | 2025-03-06 | 41097 | Cloverland Electric Cooperative | Dafter (AlphaWatt) | Load Addition | 0 | 2025-06-02 | Adjust existing metering, protection, and voltage regulator settings; commission settings when new load connects. The scope of work identified in the CEC Dafter LIRF Addition 2025 only involves distribution work, however it needs to be confirmed whether ATC system upgrades are needed to support this load addition. | 3/6/25- LIRF deemed complete and customer notified | Pirkola, Logan | TBD
45673 | 45686 | 41082 | Cloverland Electric Cooperative | Magazine (USACE DER) | Distributed Energy Resource | 12 | 2026-02-02 | Third party developer (USACE) to install a new 6.0 MW natural gas facility. CEC to connect the new facility to the distribution side of the Magazine transformer T1. ATC Scope - NCW (Note DER AFS is required) | 2/27/25- NCW letter sent to customer. Will remain on planning queue until DER AFS study is complete. 1/29/25- DERRF deemed complete and customer notified | Van Gaal, Megan | NCW - LDC Only
2021-11-19 | 2021-12-03 | 40744 | Columbus Water ＆ Light | Columbus | Xfmr Repl | 24 | 2028-06-01 | Columbus requests collaboration to determine the Best Value Plan for a variety of alternatives for replacing and/or adding a transformer in the Columbus area. ATC scope of work: Initiate BVP evaluation. Largest scope would construct a 69 kV loop through bus with switches at Maple Avenue and a 69 kV loop through bus with line breakers at Columbus South. Build 1 mile of new 69 kV line and acquire 1.4 miles of 69 kV line from Columbus. | 3/25/25 - ISD updated via Forster meeting 2/7/25- Status update sent to Forster regarding BVP drafting and next steps. 12/20/24- Submitted in Exto in Dec 2024, PI144 ​8/3/23- per internal discussions, ISD is pushed out to 6/1/26. Project is currently in a holding pattern. 12/22/21- ICC/capital work determination sent to customer 12/3/21- LIRF deemed complete and customer notified | Mainwaring, Kyle | Alternative Assessment
2025-03-18 | 2025-03-27 | 41111 | Consolidated Water Power Company | Rocky Run | High Side Protection Replacement | 0 | 2025-06-01 | CWP is going to replace breaker #399 and breaker 5-24S with newer GCB’s as a part of their relay upgrade project. ATC Scope of Work: No Capital Work (NCW) | 3/27/25- LIRF deemed complete and customer notified | Mainwaring, Kyle | NCW - LDC Support
2023-02-07 | 2023-02-21 | 40847 | Cuba City Water & Light | Cuba City - Jefferson Street | Retirement | 54 | 2031-10-15 | Cuba City to retire their Jefferson St substation with the completion of the loop-through 69 kV straight bus at their Monroe St substation. ATC will consider completing the loop-through 69 kV straight bus associated with the installation of Cuba City’s 2nd transformer. Provisions for future 69 kV line and bus-tie breakers. ATC will consider line breakers if needed. With the completion of the Monroe St loop-through bus and the retirement of Jefferson St, ATC will consider T-line routing options to loop Y-130 in and out of the Monroe St substation | 12/5/23- CW letter executed with all three phase, including retirement. ​​3/21/23- ICC email with CW determination sent to customer ​02/21/23- LIRF deemed complete and customer notified | Mainwaring, Kyle | Alternative Assessment
2024-12-20 | 2025-01-28 | 41070 | Marquette Board of Power ＆ Light | New Sub #8 | New Sub | 30 | 2026-12-31 | Marquette Board of Light and Power (MBLP) is proposing a new T-D substation with one 138-12.47 kV 20/37.3 MVA transformer on the west side of Marquette. ATC will consider installing a radial feed to new substation Consider the alternative of a 138 kV loop through straight bus with switches. | 2/27/25- initial capital work email sent to customer 1/28/25- LIRF deemed complete and customer notified | Pirkola, Logan | Alternative Assessment
2024-07-17 | 2024-07-29 | 41014 | Oconto Electric Cooperative | Greval | New Sub | 48 | 2029-07-17 | Oconto Electric Cooperative is planning to build a new T-D substation to improve grid resiliency and reinforce operation of the OEC 34.5 kV sub-transmission system. As a part of that scope, OEC to relocate idle Pioneer substation bank 2 equipment and place this equipment in service at the new Greval substation. This will provide 34.5 kV feeds though existing 34.5 kV lines to OEC Morgan, Elbe, and Underhill distribution substations. Greval to also be designed for a future second power transformer (138,000 – 7200/12,470 kV ). OEC to provide for a 138 to 7200/12470 transformer bank 2 at Greval to source 7200/12470-volt distribution feeders-tie lines to Oconto Falls, Elbe, Morgan, and Underhill distribution substations largely through existing distribution line facilities. ATC Scope of Work: ATC preliminary scope is to constructa newdouble-circuited138kV line andloop through busto serve the new substation.An ATC solution will be explored to determine the BVP: Connecting the new substation via a new tap on the MGNG81 (WCL-MGN) line. (Greater than 1 mile) or Connecting the new substation via a new tap on the NAPG63 (NAP-MGN) line. (Greater than 1 mile) | 8/27/24 - initial capital work determination sent to customer 7/29/24- LIRF deemed complete and customer notified | Mainwaring, Kyle | Alternative Assessment
2025-01-28 | 2025-02-11 | 41085 | Upper Peninsula Power Company | CR480 Substation | New Sub | 30 | 2026-10-31 | UPPCO is proposing to build a new T-D substation with one 138-12.5kV 5MVA transformer to the east of the Pineau Substation. ATC will consider installing a radial feed to new substation | 3/11/25- ICC with initial capital work determination sent to customer 2/11/25- LIRF deemed complete and customer notified | Pirkola, Logan | Alternative Assessment
2025-03-11 | 2025-03-25 | 41109 | Waunakee Utilities | Division Street | High Side Protection Replacement | 0 | 2025-12-30 | Waunakee Utilities is upgrading the fuse labeled S&C SMD-2B on drawing to a breaker for increased transformer protection and reliability at Division St substation. At a later date(Estimated 2027) they plan to upgrade the transformer to 15/28 MVA. Separate LIRF to be submitted for the transformer replacement. ATC Scope of Work: No Capital Work (NCW) | 3/25/25- LIRF deemed complete and customer notified | Mainwaring, Kyle | NCW - LDC Support
2025-03-11 | 2025-03-25 | 41110 | Waunakee Utilities | Easy Street (North) | High Side Protection Replacement | 0 | 2025-12-30 | Waunakee Utilities is upgrading the fuse labeled S&C SMD-2B on drawing to a breaker for increased transformer protection and reliability at Easy Street substation. ATC Scope of Work:No Capital Work (NCW) | 3/25/25- LIRF deemed complete and customer notified | Mainwaring, Kyle | NCW - LDC Support
2025-01-31 | 2025-02-25 | 40522-2 | Waupun Utilities | Wilson Street | New Sub | 18 | 2028-12-31 | Waupun will construct a new substation with one new 69/12.47 kV, 13.5/22.5 MVA transformer with high-side circuit breaker. Waupun will relocate the existing Comtech transformer to Wilson St. Substation. ATC will install line disconnect switches and bus-tie disconnect switches. ATC will reserve space for future install of 2 line breakers, 2 bus disconnect switches, 1 bus-tie breaker and a second 69/12.47kV transformer. ATC will retire the existing Comtech Tap and Waupun South Tap. Remove switch but pole can remain per ATC maintenance. ATC to file PSCW abandonment application. | 3/25/25 - ISD updated via Forster meeting 3/18/25- CW letter executed 2/25/25- LIRF rev2 was deemed complete and customer notified 9/17/24- ICC email sent to customer for rev1 8/19/24- LIRF rev1 deemed complete and customer notified 1/8/23- LIRF revision will be submitted soon. 10/7/21- ISD moves to 12/31/23 per discussions with Waupun and ATC planning 4/17/21- per update from Waupun, keep on in-active tab 9/30/20- ISD updated to 6/1/22 per Jim Z (18 month lead). ISD is technically TBD 5/20/20- per Steve Brooks, this project should remain on the queue 6/10/19- per Customer, project is on-hold indefinitely 07/09/18- LIRF deemed complete and customer notified | Mainwaring, Kyle | System Study
2021-08-19 | 2021-09-01 | 40711 | We Energies | Caledonia | New Sub | 36 | 2030-12-01 | WEC to construct a new Caledonia Substation with two 138/24.9 kV transformers. ATC scope of work: ATC to extend 138 kV transmission line (4-6 mi) to loop-through the new Caledonia Substation. | 12/4/24- per QP discussion, ISD moves to 12/1/30. 9/13/23- ISD moves to 6/1/30 ​​4/10/23- ISD moves to 6/1/2028 per QP meeting 9/15/22-ISD moved to 6/1/27 9/29/21- ICC email sent to customer, LIRF to reb routed at a later date 9/1/21- LIRF deemed complete and customer notified 3/4/21- added per QP meeting | Pirkola, Logan | Alternative Assessment
2024-11-22 | 2024-12-11 | 41062 | We Energies | Charter Steel | New Sub | 30 | 2028-12-31 | LDC requesting ATC to perform a sectionalizing review LDC customer requesting ATC to relocate transmission line to the north of existing line ATC to consider building a double-circuit extension with line breakers and bus-tie breaker ATC to consider relocating line to the north of existing line per request | 1/14/25- ICC email sent to customer. BVP report or CW letter to be determined. 12/11/24- LIRF deemed complete and customer notified | Pirkola, Logan | Alternative Assessment
2025-02-25 | 2025-03-07 | 41099 | We Energies | Johnson Creek | New Sub | 48 | 2028-02-25 | WEC to build a new substation in Johnson Creek, with 2 transformers and 2 busses to shift load from Concord. ATC to consider installing a 138 kV loop through straight bus with line breakers and bus-tie switches, with provisions for a future bus-tie breaker ATC to extend double-circuit 138 kV from the Crawfish River – Concord 138 kV (9043) line to the new substation. WEC is still seeking a property for this substation | 3/7/25- LIRF deemed complete and customer notified 3/13/24- ISD updated to 6/1/28 at QP meeting 2/14/22- per QP meeting, ISD moves to 6/1/26 3/4/21- per QP meeting, the ISD moves to 2025. 2/25/19- per QP meeting, ISD moves to 6/1/24 2/26/18- per QP meeting, ISD moves from 2020 to 2022 08/22/14- per QP meeting, ISD moves from 2019 to 2020 02/25/14 per QP meeting, ISD moves from 2018 to 2019 11/01/13 Customer to submit a LIRF for review | Pirkola, Logan | Alternative Assessment
2024-11-06 | 2024-11-20 | 41057 | We Energies | Lyndon | Additional Xfmr | 12 | 2027-05-31 | WEC to install a second 138-24.9kV transformer (T8) and PDC (bus 8 & 9). The high-side bus will be extended for the new transformer along with a new high-side 145kV circuit breaker and disconnect switch. WEC will vacate existing control house and move to new PDC. Existing T9 will remain, but all low-side equipment will be removed and replaced with the subsequent PDC. Existing western gate and driveway will be moved east to allow for convenient entry/exit of the substation ATC to install jumpers/rigid bus to connect to customer-owned switch for T8 | 12/20/24- MCW letter sent to customer 11/20/24- LIRF deemed complete and customer notified 3/13/24- Per QP meeting, ISD moves to 6/1/27. 3/4/21- ISD moves to 12/31/26 (was 2024 12/11/20- added per qp meeting | Pirkola, Logan | MCW
2025-02-28 | 2025-03-14 | 41102 | Wisconsin Public Service | Brusbay | Xfmr Repl | 0 | 2026-06-01 | WPS to replace existing transformers with a new transformer, replace feeder exit recloser, upgrade protective relays, and other associated work. ATC Scope - The scope of work identified in the Brusbay LIRF only identifies LDC work. No Capital Work is assumed. | 3/14/25- LIRF deemed complete and customer notified | Pirkola, Logan | NCW - LDC Only
2025-03-07 | 2025-03-21 | 41107 | Wisconsin Public Service | Clear Lake | Xfmr Repl | 18 | 2026-06-30 | WPS to replace Bank 2 transformer, replace Bank 1 & 2 circuit switchers, and other associated distribution upgrades. The scope of work identified in the Clear Lake LIRF to replace the Bank 1 & 2 circuit switchers may require jumper replacement work. | 3/21/25- LIRF deemed complete and customer notified | Pirkola, Logan | MCW
2025-02-28 | 2025-03-17 | 41104 | Wisconsin Public Service | Egg Harbor | Xfmr Repl | 18 | 2026-12-31 | WPS to replace Bank 1 and 2 transformers, upgrade protective relays, and replace high-side fuses with Circuit Switchers for Bank 1 and 2 transformers. ATC Scope of Work: The scope of work identified in the Egg Harbor LIRF to replace the high-side fuses with circuit switchers may require jumper replacement work. Minimal Capital Work is assumed | 3/17/25- LIRF deemed complete and customer notified | Pirkola, Logan | MCW
2025-03-04 | 2025-03-17 | 41105 | Wisconsin Public Service | Highway 8 | Xfmr Repl | 0 | 2026-12-31 | WPS to replace Bank 1 and 2 transformers, upgrade protective relay and feeder exit recloser. ATC Scope - The scope of work identified in the Highway 8 LIRF only identifies LDC work. No Capital Work is assumed | 3/17/25- LIRF deemed complete and customer notified | Pirkola, Logan
2025-03-17 | 2025-03-31 | 41116 | Wisconsin Public Service | James Street | High Side Protection Replacement | 18 | 2026-12-01 | WPS to replace Bank 1 circuit switcher, upgrade protective relays, RTU, and feeder exit recloser. ATC Scope - The scope of work identified in the James Street LIRF to replace the circuit switcher may require jumper replacement work. | 3/31/25- LIRF deemed complete and customer notified | Pirkola, Logan | MCW
2025-03-17 | 2025-03-31 | 41115 | Wisconsin Public Service | Oconto | High Side Protection Replacement | 18 | 2026-12-01 | WPS to replace Bank 1 and Bank 2 circuit switchers, upgrade protective relays, voltage regulators, and feeder exit reclosers. WPS requesting ATC to review if a bus-tie breaker would be warranted at the substation. Will be reviewed with ATC functional areas. | 3/31/25- LIRF deemed complete and customer notified | Pirkola, Logan | MCW
2025-02-28 | 2025-03-14 | 41103 | Wisconsin Public Service | Sister Bay | Xfmr Repl | 18 | 2026-12-31 | WPS to replace Bank 1 transformer, upgrade protective relays, replace high side fuses with Circuit Switchers for transformer Bank 1 and Bank 2, and other associated work. ATC - The scope of work identified in the Sister Bay LIRF to replace the high-side fuses with circuit switchers may require jumper replacement work (MCW). | 3/14/25- LIRF deemed complete and customer notified | Pirkola, Logan | MCW
2024-09-23 | 2024-10-10 | 41045 | Wisconsin Public Service | University | Xfmr Repl | 18 | 2026-09-01 | WPS to replace Bank 1 and 2 transformers with two (2) new base 7 MVA 69/12.47 kV transformers, replace fused high side with circuit switchers, and other distribution equipment replacements. Further outreach to WPS indicates possible replacement of high-side 69kV switches. Mobile substation required to support work. ATC Scope of Work: The scope of work identified in the University LIRF may require jumper replacement work for the high-side 69kV switches. Provide jumpered connection to mobile substation Minimal Capital Work is assumed due to the likelihood of WPS replacing their 199 and 299 switches at University SS | 12/2/24- per QP meeting, ISD is 9/1/26, before start of UWGB school year. 11/7/24- MCW letter sent to customer 10/10/24- LIRF deemed complete and customer notified 6/9/22- ISD moves to 12/1/26 per QP meeting 2/26/20- added to potential queue per QP meeting | Pirkola, Logan | MCW

## Project Management
2025-04-01
ISD has passed
ISD is within 90 days of Queue posting
LIRF/DERRF Received | LIRF/DERRF Complete | LIRF/DERRF ID # | Distribution Customer | Project Name | Project Type | Estimated ATC Project Lead-Time After PCA Execution | Requested In-Service Date | Projected Scope of Work | Notes & Updates | ATC Project Manager | BVP Type | PR # | PCA # | Construction PCA Sent | Construction PCA Signed
2022-04-27 | 2022-05-11 | 40773 | Adams Columbia Electric Cooperative | Colburn | New Sub | 36 | 2025-09-01 | ​ACEC will construct a new 69 kV substation with one 69/12.47 kV 10/14 MVA transformer with fuses for H-S protection. ATC will consider networking with a new 69 kV line from ACEC Cottonville to either Hancock or ACEC Coloma to interconnect the new ACEC Colburn Substation. Either a new switching station would be needed at the ACEC Coloma tap or Hancock would be expanded. | 1/31/25- CA filed with PSCW ​8/1/23- PM assigned and customer notified ​7/12/23-BVP report fully executed, PR submitted ​06/09/22- ICC email sent to customer, with note it will be a capital work project 05/11/22- LIRF deemed complete and customer notified | Lyons, Jason;#153 | Alternative Assessment | 9242 | N/A | N/A | N/A
2022-07-14 | 2022-07-22 | 40801 | Adams Columbia Electric Cooperative | Dixie (fka Lincoln) | New Sub | 18 | 2025-11-01 | New 69 kV substation with one 69/12.47 kV 10/12/14 MVA transformer with fuses as the H-S protection. ATC will consider installing a new 69 kV radial tap with 3 manual load break disconnect switches. | ​8/30/23- PM assigned email sent to customer ​8/10/23- PM to be reassigned, IS to reach out to ACEC with new PM. ​4/25/23- per update from ACEC, ISD moves to 11/1/25 ​2/6/23- MCW letter sent to customer, name updated to Dixie ​​2/2/23- ICC email sent to customer 7/22/22- LIRF deemed complete and customer notified ​ | Berton, Doug;#115 | Alternative Assessment | 9200 | N/A | N/A | N/A
2019-05-22 | 2019-06-17 | 40571 | Alliant Energy | Badger Pumping Station | Retirement | 18 | 2026-12-31 | Pending customer agreement, Badger Pumping substation will be retired. Load will be served from distribution service. ATC to retire 4 mile Y-38 tap from BPS to BPST, may also retire another 3.5 mile Y-38 from JAN to PHT and line terminal at JAN. | 11/8/24- PM reassigned email sent to customer 6/12/24- per QP meeting, ISD moves to 12/31/26 8/16/22- ISD moves to 12/31/24 9/16/21- per update from Bob G, ISD to be moved to 12/31/22. 3/9/21- Per QP meeting, ISD moves to 12/31/21 9/28/20- per email from Bob G, ISD moves to 6/1/21. 4/8/20- PM assigned and customer notified 4/3/20- CW Letter executed and email back to customer 6/17/19- LIRF deemed complete and customer notified | Nett, Jason;#1101 | Alternative Assessment | 8550 | N/A | N/A | N/A
2021-10-22 | 2021-11-03 | 40729 | Alliant Energy | Belleville | Sub Rebuild | 18 | 2026-12-31 | WPL will replace the existing transformer at the Belleville Substation due to age and condition and add a second transformer for reliability issues. Both transformers will be 69/24.9/12 kV 12/16/20 MVA transformers with a 2000 amp circuit breakers on the high-side. ATC will rebuild the Belleville Substation with a loop through substation insulated to 138 kV with manual line and bus-tie switches with provisions for future line and bus-tie breakers. | ​8/1/23- transitioned to project management. PM to be reassigned and IS to send email to Alliant with updated contact. ​2/14/23- executed CW letter sent to customer 8/16/22- ISD moves to 12/31/26 12/1/21- ICC email sent to customer 11/03/21- LIRF deemed complete and customer notified 6/12/19- Added to potential list during quarterly planning meeting. | Lyons, Jason;#153 | Alternative Assessment | 9170 | N/A | N/A | N/A
2021-01-08 | 2021-01-11 | 40665 | Alliant Energy | Brooklyn | Xfmr Repl | 18 | 2025-09-01 | WPL Brooklyn Transformer Replacement. ISD 12/31/2025. Alliant wants to replace the existing distribution transformer T41 at the Brooklyn Substation with a 69/24.9/12.47 kV, 10/12.5 MVA transformer, H-S fuses with a circuit breaker, and distribution reclosers with breakers. ATC will consider installing new jumpers/insulators, providing support for a portable substation and review updated drawings. | 3/6/25- ISD moves to 9/1/25 per QP meeting. 12/9/24- ISD moves to end of March 2025 5/29/24- PM assigned and customer notified. ECI will manage with oversight from Bobby L 4/25/24- revised MCW letter sent to customer 2/05/21- ICC and MCW letter sent to customer 1/11/21- LIRF deemed complete and customer notified | Lampshire, Robert;#112 | MCW | 9421 | N/A | N/A | N/A
2018-05-11 | 2018-05-31 | 40517 | Alliant Energy | Browntown | Sub Rebuild | 18 | 2025-06-01 | Two XFMRs replacement and sub rebuild on adjacent site. ATC 69 kV loop-through bus on line Y-155. Install a bus-tie switch and make provision for future line & bus-tie breakers if space allowed. | ​2/28/24- per QP discussion, ISD moves to 6/1/25 2/18/23- per Logan Brecklin and ATC project team, ISD has moved to 3/1/25 8/16/22- ISD moves to 6/1/24 1/31/22- per Greg A, ISD moves to 12/31/23 09/28/20- per email from Bob Grabow, ISD moves to 2022, ISD set at 12/31/22. 09/15/20 - ISD moves to 6/1/23 5/28/20- PM assigned and customer notified 5/11/20- CW letter executed 1/16/19- per email from Bob Grabow, ISD moves to 12/1/21. 5/31/18- LIRF deemed complete and customer notified 12/12/16- Per QP meeting, ISD moves from 09/30/20 to 9/30/25 08/8/16- per Greg in email, ISD moves from 12/30/20 to 12/01/19 02/23/16- informed via email from Alliant | Geitner, Christopher;#700 | Alternative Assessment | 8539 | N/A | N/A | N/A
2016-06-10 | 2016-06-23 | 40415 | Alliant Energy | Camp Douglas | Xfmr Repl | 24 | 2025-12-31 | Transformer Replacement | 9/26/23- ISD moves to 12/31/25 per QP discussion ​8/2/23- PM assigned email sent to customer ​6/15/23- CW letter executed ​2/2/23- Alliant shared preliminary layout with ATC via email 12/29/22- CW assessment email sent to customer, CW letter to follow. 1/31/20 - per QP meeting, ISD moves to 6/1/25 6/15/21- per QP meeting, ISD moves to 6/1/24, move back to planning queue. Alliant to resubmit LIRF if scope change 08/07/18- per QP meeting, ISD moves to 6/1/28 1/22/18- per LIRF list from Chris Allen, ISD is 2023. ISD moved to 6/1/23 and will be reviewed at first 2018 D-T check in meeting. 08/09/16- per QP meeting, project will be moved to inactive on-hold due to ISD, Planning to review project for active status on 3/1/21 06/23/16- LIRF deemed complete and customer notified | Berton, Doug;#115 | MCW | 9234 | N/A | N/A | N/A
2022-05-13 | 2022-05-27 | 40775 | Alliant Energy | Colladay Point (UW Kegonsa DER) | Distributed Energy Resource | 9 | 2025-06-01 | ​​2.25 MW solar DER will feed into the Colladay Point Transformer and Alliant will install 138kV bus VTs and apply 3V0 protection to disconnect the DER for an island condition. ATC scope of work: ATC will consider conducting insulation/protection coordination on line 13858 at Fitchburg and Kegonsa. | 12/9/24- ISD moves to June 2025 2/28/24- per QP discussion, ISD moves to 12/1/24 2/2/24- ATC ISN received for surge arrestor scope. 9/26/23- ISD moves to 06/01/2024 per QP discussion ​​4/5/23- ISD moves to 3/31/24 ​​3/1/23- PM assigned and customer notified 12/14/22- revised MCW letter sent to customer 12/7/22- updated scope sent to ATC, did not trigger a true revision. Routed to the appropriate ATC departments 06/27/22- MCW letter and ICC email sent to customer 05/27/22- DERRF deemed complete and customer notified | Meiers, Jon;#514 | MCW | 9148 | N/A | N/A | N/A
2023-04-13 | 2023-04-27 | 40858 | Alliant Energy | Cottage Grove | High Side Protection Replacement | 18 | 2026-08-01 | Alliant will retire the existing Cottage Grove substation equipment, and relocate the new substation fence to the southeast. Alliant will install a 69 kV circuit breaker, a new 69/12.47 kV, 15/20/25 MVA transformer and install a new control house with new batteries and relaying. ATC will retire the existing Cottage Grove Tap 3-way switching structure (COGT, STR 313) and replace with a new structure.ATC will retire the existing STR 139 wood pole structure, and replace with a new 3-way switching structure. | 3/6/25- ISD moves to 8/1/26 per QP meeting. 12/9/24- ISD moves to end of December 2025 2/28/24- per QP discussion, ISD moves to 06/01/25 10/26/23- PM assigned email sent to customer ​8/31/23- updated ISD per Alliant from 2026 to 2024 6/12/23- CW letter executed ​5/25/23- ICC email with CW letter sent to customer. ​4/27/23- LIRF deemed complete and customer notified 4/5/23- added to potential queue | Berton, Doug;#115 | Alternative Assessment | 9273 | N/A | N/A | N/A
2023-10-24 | 2023-11-08 | 40921 | Alliant Energy | Council Creek | Other | 18 | 2025-12-31 | Alliant to rebuild their equipment at the existing Council Creek substation. This includes: Upgrading the existing protection to a relay/breaker scheme. Replacing the existing distribution bus (appears to be 5 terminal OH setup currently) with a new 6 feeder switchgear (see provided redlined print COC-02-03). Perform maintenance on the existing transformer (replace bushings, gauges, & LTC) to extend its life. Note the primary project driver is the age and condition of the equipment. The provided prints also list that Alliant intends to replace the DPC/ALTE meter. The original one will be removed from panel 20-16 in the ATC control house and the new one will be housed in their new switchgear. Alliant plans to use a portable substation as part of this project. ATC to install new jumpers and insulators to the Alliant high side disconnect. ATC to connect/disconnect the Alliant portable substation. | 4/10/24- PM assigned and customer notified. Note - ECI will be managing this project. 2/28/24- per QP discussion, ISD moves to 12/31/25 12/12/23- ICC email with MCW letter sent to customer 10/8/23- LIRF deemed complete and customer notified | Lampshire, Robert;#112 | MCW | 9378 | N/A | N/A | N/A
2023-07-21 | 2023-08-04 | 40171-1 | Alliant Energy | Dana | Sub Rebuild | 18 | 2026-12-31 | Alliant to rebuild the existing Dana Corp (DAC) substation. This includes: Alliant to replace existing substation transformer and replace existing low side switchgear. Alliant to replace existing high side fuses with circuit switchers and will do some minor physical rearrangement of the equipment at substation site. ATC to review and adjust line protection settings if needed. Assuming it won’t be needed as the circuit switchers are an improvement from the fuses, but system protection to make final determination. ATC to relocate (or provide new) the existing dead-end structure to support the substation rearrangement. | 5/29/24- PM assigned and customer notified, will be managed by ECI with oversight from Bobby L 4/22/24- CW letter executed 9/26/23- ISD moves to 12/31/26 per QP discussion ​8/31/23- ICC email sent to WPL with CW determination, letter to follow ​08/04/23- LIRF deemed complete and customer notified 9/15/21- ISD moves from 2023 to 2024 6/12/19- ISD moves to 2023 09/11/17- ISD moves to 12/30/22 4/4/17- per Alliant, move Dana off of project management queue and place in potential, new LIRF to be submitted 02/23/16- per email from Alliant, ISD moves from 6/1/121 to 12/31/20 01/30/15- per Alliant schedule, ISD moves from 2020 to 2021 2/12/14- per Alliant, ISD moves from 6/1/17 to 2020 12/09/13 Alliant submitted a new LIRF (Pioneer) that will swap ISDs with this project; the revised ISD will change from 06/01/15 to 06/01/17 11/12/11 e-mail changing ISD from 13 to 15 | Lampshire, Robert;#112 | Alternative Assessment | 9414 | N/A | N/A | N/A
2025-02-06 | 2025-02-24 | 41032-1 | Alliant Energy | East Beloit | Sub Rebuild | 24 | 2027-12-30 | Alliant has a new load addition in the East Beloit area. Planned for approximately 8 MW. Alliant would like to relocate the East Beloit SS adjacent to the existing SS and retire the old site. City of Beloit will also be retiring their transformer at East Beloit SS in the next year or two. X-41 loop in and out. (Approx. 0.3 miles) Line breakers and provisions for a bus-tie breaker Line switches and bus-tie switches Retirement of Y-140 line from COR to ESB Retirement of East Beloit SS. | 3/13/25- PM assigned email sent to customer 3/11/25- CW letter executed 2/24/25- LIRF revised due to location update and ISD update. No major change to ATC Scope. 10/16/24- ICC email sent to customer. CW letter to follow 9/18/24- LIRF deemed complete and customer notified | Gerdes, Michelle;#930 | Alternative Assessment | PI77 | N/A | N/A | N/A
2022-10-11 | 2022-10-25 | 40814 | Alliant Energy | Gardner | New Sub | 54 | 2028-12-31 | ​WPL will construct a new138kV substation with one 138/24.9-12.4 kV 33 MVA transformer. ATC Scope of Work: ATC to construct a green field 138 kV switching station on X-42 and to build a greenfield 138 kV line to new Gardner Substation. | 12/11/24- PCA Committee met and reviewed PCA need. ATC will not proceed with a PCA for this project. 11/21/24- PM assigned and customer notified - Note BVP report in progress and to be completed. 1/22/22- ICC email sent to customer 10/25/22- LIRF deemed complete and customer notified 8/16/22- added to potential queue per D-T Check In meeting | LeMere, Tim;#827 | Alternative Assessment | 9502 | N/A | N/A | N/A
2021-12-17 | 2021-12-21 | 40746 | Alliant Energy | Gaston Road | Additional Xfmr | 24 | 2025-06-01 | Alliant will rebuild the Gaston Road Substation with two 69/12.47 kV 20/26/33 MVA transformers with high-side breakers. ATC will consider constructing a 69 kV loop through substation with line breakers and space provisions for a bus-tie breaker. | 2/13/25- ISN received for ATC scope. Confirm with WPL this project is complete or if June 2025 is still accurate. ​2/28/24- per QP discussion, ISD moves to 06/01/25 2/14/23- PM assigned and customer notified 12/13/22- CW letter executed 1/18/22- ICC email sent to customer, CW letter to follow 12/21/21- LIRF deemed complete, customer notified | Berton, Doug;#115 | Alternative Assessment | 9146 | N/A | N/A | N/A
2023-09-13 | 2023-09-27 | 40894 | Alliant Energy | Houghton Rock | Xfmr Repl | 24 | 2027-12-31 | WPL to do a complete rebuild of the Houghton Rock substation in place, including a 69/12.47 kV, 20 MVA transformer and five overhead feeders connected to the 12.47 kV bus. ATC will provide a temporary portable substation connection. ATC will install new jumpers and insulators in the newly rebuilt Houghton Rock substation. | 9/19/24- ISD update to 2027 per WPL/Greg A via email 4/9/24- PM assigned email sent to customer 2/28/24- per QP discussion, ISD moves to 12/31/26 12/4/23- per update from Ryan/Alliant, ISD moves to 12/31/25. 10/26/23- MCW letter and ICC sent to customer 9/27/23- LIRF deemed complete and customer notified ​8/16/22- added to potential queue per D-T Check In Meeting | Gerdes, Michelle;#930 | MCW | 9382 | N/A | N/A | N/A
2023-03-07 | 2023-03-16 | 40851 | Alliant Energy | Kettle Moraine | Xfmr Repl | 18 | 2025-04-30 | Alliant to retire the 138 kV circuit switcher and the existing transformer. Alliant to install 138 kV disconnect switches and a circuit breaker, and install a 10/12.5 MVA, 138/12.47 kV transformer. ATC will replace the existing 138 kV three-way switching structure with two in-line 138 kV, horizontally configured sets of switches. ATC to install new jumpers and insulators to accommodate the new Alliant high-side disconnect switch. A portable substation will be assumed, in case Kettle Moraine load cannot be bridged to Northview substation | 9/19/24- ISD update to April 2025 per WPL/Greg A via email 2/1/24- PM assigned and customer notified 1/11/24- CW letter executed for revised ATC/WPL scope ​4/13/23- MCW letter sent to Alliant ​03/16/23- LIRF deemed complete and customer notified | Pavelski, Paulo;#931 | Alternative Assessment | 9343 | N/A | N/A | N/A
2023-10-25 | 2023-11-10 | 40922 | Alliant Energy | Kieler | Sub Rebuild | 36 | 2025-12-31 | WPL Kieler rebuild project. Retiring the existing single transformer Kieler substation, and constructing a new 2-transformer ultimate substation along the planned ATC route. WPL plans to purchase and construct a new 69 kV substation with two 69/12.47 kV, 12/20 MVA transformers. WPL will make provisions for future 25 kV distribution service. ATC Scope of Work: If located a relatively larger distance away (>0.2 miles) from AY substation. New loop-through substation with manual disconnect switches (assume load-breaking attachments). ATC will provide additional loop-through transmission service along the planned Grant County DIC scope route. Retire Kieler sub termination. | 12/20/24- BVP report executed. Already with project management for precert activities. This has moved to PM. 9/19/24- revised ISD provided by Greg A via email 12/18/23- ICC sent to WPL. Will be a part of the BVP report with the other Kieler projects. 11/10/23- LIRF deemed complete and customer notified |  | Alternative Assessment | 9342 | N/A | N/A | N/A
2023-03-31 | 2023-04-04 | 40855 | Alliant Energy | Lake Geneva (Downtown) | Xfmr Repl | 24 | 2027-12-31 | ​Two alternatives include expanding the current location or relocating more north to a new substation location. Worst-case assumption – new substation.Alliant will build a new substation with one 69/12.4-24.9 kV, 20/33 MVA transformer, with ultimate plans for two transformers. ATC Scope of Work: ATC will consider installing two dead-end structures to terminate into the new Alliant substation. ATC will consider building a loop-through 69 kV bus with switches. ATC will consider retiring the 3-way GOAB devices on the LAGT tap structure, and reuse the existing structure (Jumper through) | 9/19/24- ISD updated to 2027 per WPL/Greg A via email 12/15/23- per update from Greg A via email, ISD moves to 12/31/28 (Alliant was unable to obtain the land) 11/28/23- PM assigned sent to customer 9/11/23 - CW letter is executed ​6/6/23- ISD moves to 12/31/25​ 4/21/23- ICC email sent to customer with initial CW determination ​4/4/23- LIRF deemed complete and customer notified 6/10/22- per email from Bob G, ISD moves to 2024 03/09/21- ISD moves to 12/31/23 per QP meeting 03/13/19- ISD is 2022 per QP meeting 09/11/17- ISD moves to 12/31/21 12/12/16- Per QP meeting, ISD moves from 12/31/19 to 12/31/20 08/08/16- per Greg via email, ISD moves from 6/1/19 to 12/31/19 09/3/15- per QP meeting, ISD moves form 2017 to 2019 6/2/14 Customer to submit a LIRF for review | Gerdes, Michelle;#930 | Alternative Assessment | 9288 | N/A | N/A | N/A
2020-11-06 | 2020-11-12 | 40660 | Alliant Energy | Lancaster 138kV | Additional Xfmr | 18 | 2026-03-31 | WPL will install a 138/24.9 kV 33 MVA transformer at the Lancaster Substation to connect to Y-113. Y-113 will become a 25 kV distribution line. ATC will consider retiring the 138/69 kV transformer and 69 kV bus at Lancaster and transfer line Y-113 to Alliant to use as a 25 kV line. ATC will also investigate how to provide bus separation on the 138 kV bus for the 2 Alliant transformers. | 3/6/25- ISD moves to 3/1/26 per QP meeting. 2/28/24- per QP discussion, ISD moves to 12/31/25 8/16/22- ISD moves to 12/31/24 1/11/22- PM assigned and customer notified 3/22/21- CW letter executed 3/9/21- per QP meeting, ISD moves to 12/31/23 12/10/20- initial customer communication sent to Alliant 11/12/20- LIRF deemed complete and customer notified | Osvatic, Mark;#111 | Alternative Assessment | 8799 | N/A | N/A | N/A
2020-11-06 | 2020-11-12 | 40661 | Alliant Energy | Lancaster Distribution | Xfmr Repl | 18 | 2025-12-31 | WPL will replace the existing distribution transformer with a 24.9/12.4 kV 15 MVA transformer. Y-113 will become a 25 kV distribution line. ATC scope of work: No Capital Work | 2/28/24- per QP discussion, ISD moves to 12/31/25 1/11/22- PM assigned and customer notified 3/22/21- CW letter executed 12/10/20- initial customer communicatino sent to Alliant 11/12/20- LIRF deemed complete and customer notified | Osvatic, Mark;#111 | NCW - LDC Support | 8799 | N/A | N/A | N/A
2021-10-28 | 2021-11-11 | 40730 | Alliant Energy | Mercury Marine | Xfmr Repl | 18 | 2025-12-01 | Mercury Marine to replace their T41 transformer and its supporting equipment (dead end, secondary switchgear, etc.) due to age and capacity limitations. They will also be upgrading their high side protection from fuses to a circuit breaker.As part of the upgrade Mercury looked at a few new site layouts and after some consideration they ultimately settled on relocating the new equipment slightly to the East of where it is today (see attached layout). The ATC scope of work has been narrowed down to the following:ATC to install new jumpers & insulators on the new MM dead-end structure.ATC to relocate STR 62 on line Y-60 to accommodate the relocated T41 dead-end structure (shifted closer to the T-Line pole).ATC to consider relocating STR 63 on line Y-114. This may be needed depending on where STR 62 is moved to and spacing requirements between the two lines entering the substation.ATC to consider developing a plan to connect the Y-60 feed (normally feeds T41) to T42 in the event of an extended outage on Y-114 (normally feeds T42) during the project. This was at the request of Mercury Marine and would only be used for the duration of the project.This stems from the fact that Mercury Marine was concerned that they will be on a single power feed for the duration of the project (~3 months) and an unplanned, extended down would result in costly damage to their equipment. The decision to develop this plan and the extra cost to implement will be up to Mercury Marine.The tentative thought was to implement the plan if an outage occurred that would be a lengthy fix. At that point line Y-114 would be disconnected, then line Y-60 transitioned to the Y-114 poles, and lastly terminate it to T42.A sectionalizing project was dismissed at this location due to space constraints and MM being unwilling to give up any land for the project. The thought is to add sectionalizing breakers at the Morris St. substation in the future instead. | 3/6/25- ISD moves to 12/1/25 per QP meeting. 9/19/24- ISD update to 9/2025 per WPL/Greg A via email 3/28/24- PM assigned email sent to customer 1/8/24- CW letter executed ​8/31/23- per update from WPL, ISD moves to 4/1/25 ​6/6/23- ISD moves to 12/31/25 8/16/22 - move ISD to 12/31/23 12/9/21- ICC email sent to customer 11/11/21- LIRF deemed complete and customer notified | Pericolosi, Jim;#114 | Alternative Assessment | 9368 | N/A | N/A | N/A
2023-04-10 | 2023-04-24 | 40857 | Alliant Energy | North Fond Du Lac | Xfmr Repl | 24 | 2026-06-01 | WPL to retire the existing T35 transformer. Associated high-side equipment (408-CS) and foundations will remain in place for future 2nd xfmr. WPL to replace the existing T33 transformer with a 138/12.47 kV, 20/26/33 MVA transformer, and also replace the existing 1977-CS circuit switcher with a 138 kV circuit breaker. Alliant will relocate the high side switch (1977-A) to the Alliant dead end structure, and installing new distribution switchgear. ATC Scope - MCW, ATC to install new jumpers & insulators in place of the original 1977-A switch. ATC will install new strain bus and post insulators to Alliant dead end structure and will also install new jumpers and insulators to the connect the new Alliant high side disconnect to the new ATC strain bus. | 9/27/24- ISD moves to 2026 per QP meeting. 6/12/24- per QP meeting, ISD moves to 6/1/26 4/10/24- PM assigned and customer notified. Note - ECI will be managing this project 1/24/24- MCW letter sent to customer 05/22/23- Initial CW determination sent to customer ​4/24/23- LIRF deemed complete and customer notified ​4/5/23- added to potential queue | Lampshire, Robert;#112 | MCW | 9377 | N/A | N/A | N/A
2023-11-17 | 2023-12-06 | 40930 | Alliant Energy | Northgate | Sub Rebuild | 12 | 2025-12-31 | Alliant to rebuild the Northgate substation on the existing site. The low side distribution equipment will be upgraded to a 7 feeder switchgear. Additional SCADA/control capabilities will be added to the substation with the project. The high side equipment and transformer will be left as is. The LIRF notes a portable substation will be required as part of this project. ATC to perform the connection/disconnection of the portable substation. Alliant ownershipdoes not start immediately after the tap structure, our EMS is incorrectly labeled. | 4/10/24- PM assigned and customer notified 2/28/24- per QP discussion, ISD moves to 12/31/2025 1/9/24- MCW letter and ICC email sent to customer 12/6/23- LIRF deemed complete and customer notified | Lampshire, Robert;#112 | MCW | 9372 | N/A | N/A | N/A
2020-11-06 | 2020-11-12 | 40658 | Alliant Energy | Oxford | Additional Xfmr | 18 | 2027-12-31 | WPL will install a new 69/12.47 kV 9.375 MVA transformer, distribution feeders, and 2000-amp circuit breaker at the Oxford substation. WPL will retire Neenah Creek transformer, distribution bus, and reroute the distribution feeders to the Oxford Substation. ATC to retire Neenah Creek tap and remove the existing Neenah Creek tap 3-way switch. ATC to expand the Oxford 69kV Bus to north andprovide jumpers and insulators to allow the new WPL transformer to be interconnected to Oxford 69kV bus. | 3/13/25- PM assigned email sent to customer 12/20/24- Submitted in Exto in Dec 2024, PI139 9/27/24- ISD moves to 12/31/27 per update at QP meeting 9/16/24- CW letter executed 2/28/24- ISD moves to 12/31/26 per QP discussion. 12/4/23- per update from Ryan/Alliant, ISD moves to 12/31/25 1/31/22- per QP meeting, ISD moves to 12/31/26 6/15/21-ISD moves to 12/31/25 per QP meeting 12/10/20- ICC email sent to customer 11/12/20- LIRF deemed complete and customer notified | Ford, Chad;#1103 | Alternative Assessment | PI139 | N/A | N/A | N/A
2024-03-07 | 2024-04-09 | 40583-1 | Alliant Energy | Pleasant View | Sub Rebuild | 24 | 2027-12-31 | WPL to replace T31 and T32 to 138/24.9kV 30/40/50 MVA rated transformers along with the associated switchgear. WPL will replace the circuit switchers to circuit breakers on 138kV sides for T31, T32 and T33. WPL will relocate ATC’s and WPL’s relay connections to the new breakers. (Described in B2-N16112C one line diagram page of the attached project binder) System Protection team needs to review and verify if they agree with this. ATC will consider providingnew jumpers and insulatorsfor the new disconnect switch on high side of T31 and T32. No physical scope expected for ATC on high side of T33.Modify existing ATC bus differential relays on bus 1 and bus 2 to terminate into the new breaker CTs | 8/14/24- PM assigned and customer notified. Will be managed by ECI staff, with oversight from Bobby Lampshire. 5/7/24- MCW letter and ICC sent to customer 4/9/24- LIRF rev deemed complete and customer notified ​​4/5/23- ISD moves to 12/31/26 8/16/22- ISD moves to 12/31/25 2/5/21- ICC and MCW letter sent to customer 12/1/20- per QP meeting, ISD moves to 12/31/24 9/9/19- LIRF deemed complete and customer notified | Lampshire, Robert;#112 | MCW | 9456 | N/A | N/A | N/A
2024-05-01 | 2024-05-17 | 40981 | Alliant Energy | Potosi | Retirement | 12 | 2025-12-31 | WPL will retire Potosi interconnection once Tennyson is in service and all feeders Potosi feeders cut over to Tennyson. ATC to install a few 138 kV transmission line pole on the Nelson Dewey – Tennyson 138 kV line (X-15) to allow the retirement of the existing Potosi tap structure (STR 128) and Potosi tap conductor. | 10/24- Assigned to contract PM- Christopher Fredrick with oversight from Bobby Lampshire. 9/19/24- ISD moved to 2025 per email from WPL/Greg A 5/22/24- PM assigned and customer notified 5/17/24- LIRF deemed complete and customer notified | Lampshire, Robert;#112;#Frederick, Christopher;#880 | Alternative Assessment | 9416 | N/A | N/A | N/A
2023-09-13 | 2023-09-27 | 40893 | Alliant Energy | Poynette | Xfmr Repl | 24 | 2027-12-31 | Alliant to rebuild the existing Poynette Substation in place. The rebuild appears to be a one for one replacement of the existing equipment at this point. LIRF lists that Alliant will be providing a portable substation as part of the project. ATC to perform the connection on the portable substation. ATC to install new jumpers & insulators on the Alliant dead end structure. ATC to relocate the existing Poynette tap switch, see the project notes section for reasoning. The relocation involves retiring the existing Poynette tap switch structure, installing a new Poynette tap switch structure, installing six new T-Line poles, and installing the necessary conductor (~ 0.26mi) for the reroute. | 3/6/25- ISD moves to 12/31/27 per QP meeting. 10/24- PM reassigned, Theodore Tolish (contract PM) with oversight from Bobby Lampshire 6/12/24- per QP meeting, ISD moves to 4/30/27 6/7/24- PM assigned and customer notified- S&L will PM with oversight from Mark Osvatic 5/6/24- CW letter executed 2/28/24- ISD moves to 2027 per QP meeting 10/27/23- ICC email sent to customer. CW letter to be executed at later date. 9/27/23- LIRF deemed complete and customer notified ​8/16/22- added to potential project per D-T Check In Meeting | Lampshire, Robert;#112;#Tolish, Theodore;#1006 | Alternative Assessment | 9434 | N/A | N/A | N/A
2021-03-04 | 2021-03-15 | 40690 | Alliant Energy | Shullsburg | Xfmr Repl | 18 | 2025-06-01 | Alliant wants to replace the existing Shullsburg distribution transformer with a 69/12.5 kV, 5.25 MVA transformer. ATC scope of work: ATC will consider providing support for a portable substation. | 3/6/25- ISD moves to 6/1/25 per QP meeting. 9/19/24- per email from Greg A, this project ISD has moved to 4/30/25 ​4/5/23 - ISD moves to 12/31/25 1/31/22- per Greg A, ISD moves to 12/31/23 7/9/21- PM assigned and customer notified 6/15/21- ISD moves to 12/31/22 4/12/21- MCW letter and ICC sent to customer 3/15/21- LIRF deemed complete and customer notified | LeMere, Tim;#827 | MCW | 8855 | N/A | N/A | N/A
2016-08-10 | 2016-08-19 | 40397-1 | Alliant Energy | South Lake Geneva | Additional Xfmr | 24 | 2026-12-31 | New ATC jumpers | 2/28/24- per QP discussion, ISD moves to 12/31/26 8/16/22- ISD moves to 12/31/27 1/31/22- per Greg A, ISD moves to 12/31/25 09/15/20 - per QP meeting, ISD moves to 12/31/24 10/9/19- per QP meeting, ISD moves to 12/31/23 08/19/16- LIRF Rev 1 deemed complete and customer notified 08/08/16- per Greg's via email ISD moves from 10/01/17 to 12/31/22 08/02/16- transitioned to Project Management, customer notified 04/19/16- MCW determination letter was emailed to the customer 03/03/16- LIRF deemed complete and customer notified | Hanold, Nick;#102 | MCW | 7478 | N/A | N/A | N/A
2021-11-05 | 2021-11-19 | 40737 | Alliant Energy | Stoughton | Retirement | 18 | 2027-12-31 | Alliant wants to retire transformer T41 and all associated distribution equipment at the Stoughton Substation. ATC will consider retiring the jumpers going into switch 695-A. | 12/09/24- per WPL, ISD moves to 12/31/27 5/17/24- PM assigned and customer notified 4/22/24- PR submitted 12/14/21- ICC and MCW letter sent to customer 11/19/21- LIRF deemed complete and customer notified | Hughes, Patrick;#1011 | MCW | 9413 | N/A | N/A | N/A
2024-05-01 | 2024-05-17 | 40887-1 | Alliant Energy | Tennyson | Sub Rebuild | 18 | 2025-12-31 | WPL will install a new 138/24.9/12.5 kV, 10/12.5 MVA transformer to replace Potosi transformer. WPL to install high side disconnect switch and circuit breaker for xmfr protection. ATC to add a disconnect switch and a ring-bus breaker on ATC 138 kV bus #3. | 10/24- Assigned to contract PM- Christopher Fredrick with oversight from Bobby Lampshire. 5/22/24- PM assigned and customer notified 5/17/24- LIRF rev 1 deemed complete, no change to pending PR 4/19/24- CW letter executed 12/13/23- name updated to Potosi/Tennyson per QP meeting with Alliant 10/18/23- ICC email sent to customer, CW letter to follow. 9/20/23- LIRF deemed complete and customer notified | Frederick, Christopher;#880;#Lampshire, Robert;#112 | Alternative Assessment | 9416 | N/A | N/A | N/A
2023-09-13 | 2023-09-27 | 40892 | Alliant Energy | Tomah Industrial Park | New Sub | 24 | 2026-05-01 | WPL to retire the existing Tomah Industrial Park substation. WPL to construct a new Tomah Industrial Park substation to the west of the existing site, and install a 33 MVA, 69/24.9-12.47 kV transformer. Five overhead distribution feeders will exit the low-side bus. ATC will retire the existing 32a dead-end structure. ATC will install a new dead-end structure to terminate into the new Tomah substation. ATC will provide jumpers and insulators to terminate into the WPL dead-end structure within the substation. | 9/19/24- ISD moves to 5/26 per WPL/Greg A via email 5/29/24- PM assigned and customer notified. Will be managed by ECI, with oversight from Bobby L 4/26/24- MCW letter sent to customer 2/28/24- per QP discussion, ISD moves to 12/31/26 10/27/23- ICC email sent to customer. Capital work letter to be executed at a later date. 9/27/23- LIRF deemed complete and customer notified 8/16/22- added to potential queue to D-T queue check in​ | Lampshire, Robert;#112 | Alternative Assessment | 9423 | N/A | N/A | N/A
2021-04-13 | 2021-04-27 | 40696 | Alliant Energy | Vienna | Additional Xfmr | 18 | 2026-12-31 | Alliant plans to add a 138/25/12.47 kV, 20/26/33 MVA transformer with a high-side circuit breaker at the Vienna Substation. Alliant also plans to replace the high-side circuit switcher on the existing transformer with a circuit breaker. ATC will consider installing line breakers, providing new jumpers/insulators for the transformer addition, and support for a portable substation. | 12/13/23- per email from Greg A, ISD moves to 12/31/26 ​6/29/23- PM assigned and customer notified ​4/28/23- CW letter executed 8/16/22- ISD moves to 12/31/25 5/15/21- ICC email sent to Alliant 4/27/21- LIRF deemed complete and customer notified | Nyman, Garrett;#757 | Alternative Assessment | 9218 | N/A | N/A | N/A
2023-06-29 | 2023-06-30 | 40722-1 | Black Earth Utilities | Black Earth Substation | Additional Xfmr | 36 | 2025-09-01 | BEEU will install one 69/12.47 kV 7.5/10.5 MVA transformer with either power fuses or a transruptor at the existing Black Earth substation. ATC scope of work:ATC will consider installing a temporary structure to transition the Y-62 line into the new transformer as an emergency support capability. ATC will retire the existing Black Earth Tap (BLET) three-way switching structure. ATC will consider installing a 69 kV box structure to support a loop-through connection in this smaller substation footprint. ATC will install two line circuit breakers with the associated bus and line-side disconnect switches. | 3/25/25 - ISD is sometime in Fall 2025, per Forster meeting. 2/1/24- PM assigned email sent to customer 12/5/23- PR submitted 12/1/23- CW letter fully executed 9/8/23- BEEU provided updated information, including ISD, via LIRF. LIRF not treated as a revised LIRF. ​7/13/23- ICC email wiith CW determination sent to customer. CW letter to follow for rev 1 06/30/23- LIRF rev1 deemed complete and customer notified 10/19/21- ICC email with CW determination sent to customer 9/22/21- LIRF deemed complete and customer notified | Pavelski, Paulo;#931 | Alternative Assessment | 9323 | N/A | N/A | N/A
2024-12-20 | 2025-01-07 | 41071 | Brodhead Water ＆ Light | Brodhead Muni 1 | Retirement | 12 | 2025-06-01 | Brodhead has completed a significant portion of conversion away from 4 kV. Brodhead will decommission the Muni 1 Substation. Brodhead is requesting to take ownership of the wood transmission pole outside the substation after removal of 69 kV line, since Brodhead has under-built distribution infrastructure.. ATC will de-energize and remove the transmission tap that serves this substation. (except structure 2A) ATC to file abandonment application with PSCW ATC to transfer ownership of structure 2A to Brodhead. Due to the timeframe requested by the customer and required abandonment application, Forester agreed to open the high-side switch at the station which would allow Brodhead to remove their equipment prior to ATC’s abandonment. | 3/25/2025 - Subs are deenergized. ISD reflecting decomissiong and ATC abandonment process 3/13/25- PM assigned email sent to customer January 2025- added in Exto - PI151 01/28/25- MCW letter sent to customer 1/7/25- LIRF deemed complete and customer notified | Gerdes, Michelle;#930 | MCW | PI151 | N/A | N/A | N/A
2024-12-20 | 2025-01-07 | 41072 | Brodhead Water ＆ Light | Brodhead Muni 2 | Retirement | 12 | 2025-06-01 | Brodhead has completed conversion away from 4 kV. Brodhead will decommission the Municipal Substation 2 transformer. Brodhead will remove the transformer, and other distribution equipment. The substation steel structures will remain in place for potential future use. There are no current plans to utilize the site, but it will retained for future use. ATC will de-energize and remove the transmission tap that serves this substation. ATC to file abandonment application with PSCW Due to the timeframe requested by the customer and required abandonment application, Forester agreed to open the high-side switch at the station which would allow Brodhead to remove their equipment prior to ATC’s abandonment. | 3/25/2025 - Subs are deenergized. ISD reflecting decomissiong and ATC abandonment process 3/13/25- PM assigned email sent to customer January 2025- added in Exto - PI151 01/28/25- MCW letter sent to customer 1/7/25- LIRF deemed complete and customer notified | Gerdes, Michelle;#930 | MCW | PI151 | N/A | N/A | N/A
2024-05-02 | 2024-05-22 | 40985 | Central Wisconsin Electric Cooperative | Sannes | High Side Protection Replacement | 9 | 2024-12-31 | CWEC is replacing high-side structure for the fuse. Substation fence will be expanded to the west to allow space to bring in a mobile sub when needed. ATC to consider removing structure 2S and connect structure 1S to the new CWEC high-side structure (or disconnect switches) with new jumpers and insulators. | 8/20/24- PM assigned and customer notified 7/24/24- PR submitted 7/16/24- MCW letter sent to customer 5/22/24- LIRF deemed complete and customer notified | Nettesheim, Justin;#105 | MCW | 9473 | N/A | N/A | N/A
2013-05-30 | 2013-06-03 | 40300 | Cloverland Electric Cooperative | Kincheloe | New Sub | 24 | 2024-12-31 | Retire main & housing SS; putting in 1 new SS | 10/15/24- per update from Brian, ISD moves to 12/31/24 5/2/24- updated one line provided to ATC by CEC 1/8/24- per update from BL, transformer will be delivered in October 2024 and load from the old station to the new sub will be shifted in 2025. 1/25/21- per PM, ISD is 3/1/24. Discussed PCA and determined PCA would not be required for this project 9/20/21- per BL, ISD to remain 1/1/24 2/16/21- per email from LDC, ISD is 1/1/24 5/2/18- per CEC, ISD moves back to 1/1/23 07/28/17- per customer email, ISD moves from 1/1/20 to 1/1/21 01/21/16- per email from Steve, project remains on hold and ISD moves from 1/1/18 to 1/1/20. 05/07/15- per email from Steve, project is on hold and ISD moves to 1/1/18.8/26/14- per customer, ISD moves from 1/1/16 to 1/1/7, with construction starting in 2-16 1/21/14- ISD changes from 1/1/15 to 1/1/16 12/26/13 per Cloverland, the ISD was changed from 01/01/15 to 01/01/16 11/04/13 PCA being drafted with Cloverland | Pericolosi, Jim;#114 | MCW | 6107 | N/A | N/A | N/A
2022-10-17 | 2022-10-31 | 40816 | Cloverland Electric Cooperative | Manistique Pump Station | Xfmr Repl | 18 | 2025-03-31 | ​CEC to relocate the existing Lakehead Manistique substation closer to ILKY51. ISD 12/31/2024. CEC will relocate substation due to age and condition of the existing transformer and a desire to move outside of the Enbridge Fence.The new substation will include a new 69/4.16 kV 7.5 MVA transformer to provide dedicated service to Enbridge. ATC will remove two transmission towers (146481-146482) and consider installing a single 69kV dead end, as well as terminate jumpers into the new substation. | 10/15/24- per discussion with CEC - ISD will be 3/1/25, possibly closer to May 2025 - TBD. 10/26/23- PM assigned email sent to customer ​11/30/22- ​CW determination and ICC response sent to customer 10/31/22- LIRF deemed complete and customer notified | Pericolosi, Tony;#701 | MCW | 9276 | N/A | N/A | N/A
2023-02-07 | 2023-02-21 | 40812-1 | Cuba City Water & Light | Cuba City - Monroe Street | Additional Xfmr | 24 | 2024-09-15 | Cuba City to install 2nd distribution transformer at Cuba City South (Monroe St.) and requesting half of loop-through high side bus be constructed with Phase 1. Phase 2 will complete loop-through bus configuration. ATC will consider installing half of a loop-through 69 kV straight bus associated with the installation of Cuba City’s 2nd transformer. Initial bus installation to leave provisions for future 69 kV line breaker. Future state is 69 kV loop-through straight bus with 2 line breakers and space for a bus-tie breaker. ATC will consider replacing existing 69 kV line from Roaster Road to the existing Cuba City Monroe St Substation with a double circuit line to prepare for Phase 2. | 2/12/24- PM assigned email sent to customer 12/6/23- PR submitted 12/5/23- CW letter for phase 1 & 2 executed 9/25/23- CW letter executed ​3/21/23- ICC email with CW determination sent to customer ​02/21/23- LIRF rev 1 deemed complete and customer notified ​11/15/22- CW assessment/ICC sent to customer 10/18/22- LIRF deemed complete and customer notified | Nyman, Garrett;#757 | Alternative Assessment | 9327 | N/A | N/A | N/A
2025-02-24 | 2025-02-25 | 40881-2 | Evansville Water ＆ Light | Union Townline Substation | Additional Xfmr | 24 | 2027-03-01 | ​WPPI/Evansville Water & Light to install a second 69/12.47kV 12/22.4MVA transformer at the Union Townline Substation (UTL). A circuit switcher will be installed for high side protection. Low side bus, feeder terminals, and a bus tie switch (load break) will be installed. ATC to install approximately 0.08 miles of 69kV line to tie the new transformer to Y-158. ATC to install a new dead end structure in the substation for the new line. ATC to install a new high side loop through bus configuration. ATC to install line breakers and associated control house and provisions for a future bus tie breaker. ATC to remove the existing Union Townline Tap (UTLT) three way switching structure. ATC to relocate the dead end structure of the existing substation feed to make room for the new high side bus and sectionalizing equipment. | 2/25/25- LIRF rev2 deemed complete and customer notified. 1/30/25- Evansville received CA approval from PSCW for load addition 12/27/24- transitioned to PM 10/3/24- CW letter executed 9/16/24- CW letter rev1 sent for execution to Evansville. 5/15/24- ICC email sent to customer. CW letter rev1 to follow. 4/17/24- LIRF rev1 deemed complete and customer notified 4/8/24-CW letter executed 11/10/23- Nick discussed equipment lead time issues with customer. ISD moved to 5/1/26 with approval from customer ​8/21/23- ICC email with CW determination sent to customer ​7/26/23- LIRF deemed complete and customer notified | Groeschel, Wayne;#1102 | Alternative Assessment | 9531 | N/A | N/A | N/A
2023-01-05 | 2023-01-19 | 40841 | Madison Gas ＆ Electric | Syene (Tyto Solar) | Distributed Energy Resource | 12 | 2023-10-15 | MGE will interconnect 6.6 MW of new solar DER to an existing 13.8 kV feeder. ATC Scope - Upgrade surge arresters on Nine Springs-Pflaum 69 kV line (6947) and Pflaum-Royster 69 kV line (6934). The following surge arrestors should be upgraded with the project: Nine Springs C1 Cap Bank (8060-CS) & Nine Springs C2 Cap Bank (8061-CS). | 4/10/24- PM assigned and customer notified, note this project is managed by ECI 4/9/24- per QP meeting, DER is energized. Will move to PM shortly for surge arrestor replacements. 3/12/24- updated MCW letter sent to customer 1/2/23- Planning confirmed ICCP data was received for EMS. PR to be written for surge arrestor replacements. 10/10/23- per MGE, this DER will be energized in mid October 2023. Testing and commissioning will then commence. ​2/10/23- MCW letter and ICC sent to customer ​1/19/23- DERRF deemed complete and customer notified | Lampshire, Robert;#112 | MCW | 9375 | N/A | N/A | N/A
2023-09-19 | 2023-10-04 | 40896 | Mazomanie Electric Utility | Mazomanie West | Additional Xfmr | 18 | 2025-11-30 | Mazomanie to install a second transformer (69/12.47kV, 15/20/25MVA) and the supporting LDC owned bus/equipment at the Mazomanie West substation. The primary need driver here is to improve redundancy and reliability by having a backup transformer. Per the LIRF, Mazomanie can no longer transfer the entire load from the existing transformer in the event of maintenance or an outage. ATC to install new insulators on both the existing ATC open terminal dead-end structure and the new Mazomanie dead-end structure and then install T-Line/jumpers to connect the two. | 3/25/25 - ISD is sometime in Fall 2025, per Forster meeting 4/11/24 - PM assigned, will be project managed by ECI 11/7/23- MCW letter sent to customer 10/4/23- LIRF deemed complete and customer notified | Lampshire, Robert;#112 | MCW | 9370 | N/A | N/A | N/A
2022-11-10 | 2022-11-29 | 40682-1 | Plymouth Utilities | Plymouth #5 | New Sub | 36 | 2025-09-01 | Plymouth Utilities will construct a new Plymouth #5 Substation near the intersection of County Roads A and V to support the expansion of the ANR Pipeline facility. ATC will facilitate a BVP study process. ATC will consider constructing a new double circuit 138 kV line (approx. 5 to 7 miles) to loop through Plymouth's new substation. | 9/28/23- BVP executed ​​4/17/23- PM - Mark Osvatic - has been assigned as a part of the enhanced scoping effort, PM assigned email sent to customer 12/29/22- CW determination/ICC email sent to customer 11/29/22- LIRF rev 1 deemed complete and customer notified 3/17/21- ICC email sent to customer 2/17/21- LIRF deemed complete & customer notified | Mainwaring, Kyle;#119 | Alternative Assessment | 9175 | ​2023-002 | ​07/12/23 | ​07/21/23
2024-12-02 | 2024-12-17 | 40760-1 | Reedsburg Utility Commission | Artesian | Other |  | 2026-03-31 | Reedsburg Utility Commission (RUC) is planning to rebuild RUC-owned 69 kV circuit Y-162 from Webb Substation to the Grede West switch R6920-A. With the retirement of ATC’s Reedsburg Substation, Y-162 becomes the primary feed for Reedsburg’s Webb Substation. ATC Revised Scope: ATC will reconfigure line Y-53 Install 2 new 3-way GOABs with Load break switches Construct approximately 0.35 miles of new 69 kV line Retire approximately 1.11 miles of line ATC will move breaker 2397-S to the 2394-S position to support the new BA metering point at Artesian SS | 3/25/2025 - ISD updated to match project schedule 12/17/24- LIRF rev1 has been reviewed, deemed complete and customer is notified. LIRF will not be rerouted as there is a project team already working on this scope. The revised LIRF is for documentation purposes. ​8/3/23- ISD updated to 9/1/24 per internal discussions. 1/31/23- per update from Crystal, ISD moves to end of 2023, may push into Q2 2024. Check in later in year. ​3/15/22- PR 8949 submitted for related Reedsburg retirement projects (ATC only) 3/9/22- TIRF information moved to LIRF form and communicated to customer. Artesian project information is now housed on D-T queue and in LIRF folders (previously submitted via T-T interconnection process 1/11/22- PM assigned and customer notified. 11/5/21- MCW letter provided to customer. 3/11/21- TIRF deemed complete and customer notified. | Pericolosi, Tony;#701 | Alternative Assessment | 8947 | N/A | N/A | N/A
2022-04-08 | 2022-04-22 | 40768 | Rock Electric Cooperative | Johnstown | New Sub | 24 | 2026-03-31 | REC will construct a new 138 kV substation with one 138/24.9 kV 15/25 MVA transformer with either a circuit switcher or circuit breaker for H-S protection. ATC will consider constructing a new 138 kV loop through straight bus on line 4434 with 2 line breakers and space provisions for a future bus-tie breaker. | 11/8/24- PM reassigned email sent to customer ​5/14/24- ISD moves to 3/31/26 due to material delays. 1/31/23- PM assigned email sent to customer 05/20/22 ICC email with CW determination emailed to customer. 04/22/22- LIRF deemed complete and customer notified | Nett, Jason;#1101 | Alternative Assessment | 9151 | N/A | N/A | N/A
2022-11-18 | 2022-12-06 | 40184-1 | UMERC | Keel Ridge | New Sub | 24 | 2025-12-01 | UMERC is proposing a new T-D interconnection substation with a new 14 MVA, 69/13.8 kV distribution transformer. High-side protection TBD. ATC will consider tapping the Armory – Big Quinnesec Falls 69 kV (6820) and constructing ~0.5 miles of a radial tap to the proposed T-D substation location. ATC will also consider installing a 69 kV line breaker at Armory to sectionalize the line. | ​​6/19/23- moved to PM, Tony Pericolosi is ATC PM. PM assigned email sent to WPS ​3/3/23- CW letter executed ​1/6/23- ICC/CW determination for rev1 sent to customer 12/6/22-LIRF rev 1 deemed complete and customer notified 9/29/21- ISD moved to 6/1/25, revised LIRF to be submitted 3/23/21- per QP meeting, ISD moves to 6/1/27, remains on inactive queue 07/16/20- PM reassignement email sent to UMERC 3/7/19- ISD moves to 6/1/24 08/07/18- per Steve P, this project is on hold. Earliest ISD is 2022 03/10/17- per QP meeting, ISD moves to 2022. 11/30/16- Per QP meeting, ISD moves from 6/1/19 to 6/1/20 08/26/15- land has been chosen and procurded. Next step is the PCA 02/12/15- per QP meeting, ISD moves from 2017 to 6/1/19 08/29/14- per WEPCo, ISD moves from 12/1/17 to 10/1/17 05/23/14- per WEPCo at QP meeting, site has been pinned down, working through logistics with landowner 05/20/14- PCA process to begin once a sight is chosen 1/22/14- per M. Burow, PCA will be needed 09/17/13 WEPCo submitted a revised ISD of 12/01/17 09/19/12 per WEPCo, a site has not been chosen so the PCA process will begin at a later date | Pericolosi, Tony;#701 | Alternative Assessment | 4698 | N/A | N/A | N/A
2022-12-06 | 2022-12-20 | 40835 | Upper Peninsula Power Company | Delta | Xfmr Repl | 18 | 2025-09-01 | UPPCO will replace the Bank 1 transformer with a 69/12.47 kV, 12/14/16 MVA transformer UPPCO will also replace the high-side disconnectswitch, and replace existing fuses with a high-side breaker (similar configuration to Bank 2). ATC will consider installing new jumpers and insulators to the new UPPCO 69 kV high-side disconnect switch, and modify the ATC bus protection with the new high-side breaker. | ​04/05/23- per UPPCO, ISD moves to 9/1/25. Logan alerted PM Jim P. ​2/22/23- PM assigned and customer notified ​1/23/23- MCW letter sent to customer 12/20/22 - LIRF deemed complete and customer notified 5/9/22 Per QP meeting ISD updated to 12/31/22 5/8/20- added as potential project per Tim K | Pericolosi, Jim;#114 | MCW | 9167 | N/A | N/A | N/A
2022-11-03 | 2022-11-03 | 40228-2 | Upper Peninsula Power Company | Perch Lake | Additional Xfmr | 18 | 2024-12-31 | UPPCO to interconnect a new 138/12.47 kV, 5/7 MVA transformer to the spare 138kV bus position 2. UPPCO to install 12.47 kV switching equipment to tie the existing and new transformer together. ATC Scope of Work: The existing 2201 switch owned by will be transferred to UPPCO. ATC will modify the bus protection design to account for the new interconnection. ATC to remove ATC-owned 138 kV SSVT and connect into the 2nd UPPCO station service source on the new transformer. | 10/2/24- per QP meeting, ISD moves to 12/31/24 12/14/23- PM assigned email sent to UPPCO 10/23/23- MCW letter sent to customer and PR submitted 12/05/22- NCW letter sent to customer 11/3/22- LIRF rev 2 deemed complete and customer notified 10/5/22- per QP meeting, ISD moves to 6/1/24 10/26/21- Scope updated per UPPCO QP meeting 2/1/21 - per updates from Tim/UPPCO, ISD moves to 11/1/23 11/16/20- Initial customer communiction sent to UPPCO 10/23/20 - LIRF deemed complete and customer notified 4/15/20 - ISD moves to 12/1/24 5/2/19- per UPPCO capital plan, ISD is TBD 4/15/19- per QP meeting, ISD moves to 6/1/22 10/20/17- per QP meeting, this can be moved back to planning, ISD is now 6/1/21 07/10/13 per UPPCO, on hold 01/05/12 informed UPPCo LIRF is complete | Baij, Janssen;#817 | MCW | 9290 | N/A | N/A | N/A
2023-12-14 | 2024-01-02 | 40947 | Upper Peninsula Power Company | Timber Products | Load Addition | 0 | 2025-03-31 | A third party customer is planning an operational expansion which will add ~2.4MW of load to the Timber Products substation. The actual MVAR demand/power factor are still unknown, but LDC states they will discuss potential power factor correction with the customer. The load addition includes several motors; the largest is 150HP and will be on a VFD, the largest that will potentially be started across the line is 100HP. At this time UPPCO plans to add fans to their existing transformer to increase capacity to support the added load. ATC Scope of Work: A preliminary review by Michael B. found thermal issues in the area for two N-1-1 scenarios. The thermal issues were driven primarily by low voltages. Both were resolved with the completion of the Munising Statcom (2026 ISD). Temporary mitigation issues are still being discussed. Note the review included the proposed 2.5MW load addition at KI Sawyer (ISD 3/1/2024). ATC to install a mobile capacitor bank to support the added load until the Munising Area Reactive Power Project (MTEP Project ID 19966) is placed in service, targeted for January 2026. | 2/21/25- per update from Jason S at UPPCO, elective facilities work will not be pursued at this time. 10/2/24- per update at QP meeting, ISD moves to end of Q1 2025. 9/4/24- ISN received for mobile cap bank at Munising. 5/30/24- PM assigned and customer notfied 4/18/24- MCW letter sent to customer 1/2/24- LIRF deemed complete and customer notified | Siegler, Dorn;#116 | MCW | 9420 | N/A | N/A | N/A
2023-12-12 | 2023-12-20 | 40937 | Wisconsin Public Service | 7th Street | Additional Xfmr | 12 | 2025-07-31 | WPS to install a new (third) feeder at the 7th Street substation. This includes a high side circuit switcher, a 138/24.9kV 22.4MVA transformer, and the associated distribution equipment. The WPS high side disconnect (switch 299) and the equipment foundations are already installed. ATC to install a second bus tie disconnect switch adjacent to the existing BTG1 disconnect in preparation for a future breaker. The load on the two feeders will already be high (~20MW) and this eliminates the need for a future outage when we go to install a bus tie breaker. ATC to perform necessary protection modifications to support an additional distribution transformer. | 12/2/24- per QP meetings, ISD moves to 7/31/25 7/24/24- ISD updated to 3/31/25 per QP meeting with WEC North. 4/10/24- PM assigned email sent to customer- note this project is managed by ECI 1/9/24- MCW letter and ICC email sent to customer 12/20/23- LIRF received and deemed complete 12/4/23- ISD moves to 2/1/25 9/6/18- per QP meeting, ISD moves to 6/1/25 3/9/18- ISD moves to 2024 per QP meeting 09/15/15- Per QP meeting, ISD moves from 2019 to 2023 06/12/14- per QP meeting, ISD moves from 6/1/17 to 6/1/19 11/01/13 Customer to submit a LIRF for review | Lampshire, Robert;#112 | MCW | 9373 | N/A | N/A | N/A
2023-04-24 | 2023-05-22 | 40865 | Wisconsin Public Service | Algoma | Xfmr Repl | 18 | 2025-12-01 | WPS is proposing to replace existing distribution transformer T1 with a new 69/24.9 kV, 26/30 MVA unit. High-side fuse to be replaced with a breaker or circuit-switcher. ATC - MCW - replace insulators/jumpers for new high-side device. | 4/10/24- PM assigned email sent to customer. Note - ECI is managing this project. 2/20/24- ISD moved back to 2025, PR to be drafted. 9/13/23- ISD moves to 2027 ​6/16/23- MCW letter sent to customer ​5/22/23- LIRF deemed complete and customer notified 12/3/20- ISD moves from 12/1/24 to 12/1/25 2/26/20- Added to potential queue per QP meeting | Lampshire, Robert;#112 | MCW | 9362 | N/A | N/A | N/A
2024-12-30 | 2025-01-15 | 40863-1 | Wisconsin Public Service | Dunn Road | Xfmr Repl | 0 | 2026-06-01 | WPS is proposing to replace existing distribution transformer bank 1 with a new 69/24.9 kV, 26/30 MVA unit. A new high-side disconnect switch (199) will be installed on its own structure. The existing circuit switcher (199) will be removed and a new 69kV gas circuit breaker will be installed. ATC to extend 69 kV bus and install jumpers to connect to customer owned switch for new Bank 1 transformer | 3/10/25- PM assigned and customer notified 2/13/25- entered into Exto - PI155 2/13/25- CW letter executed by WPS 2/7/25- CW letter sent to WPS for execution 1/15/25- LIRF rev1 deemed complete and customer notified 2/14/23 - Notified by Drew Bain that Dunn Rd XFRM replacement work has moved back up into 2025, change ISD to 12/1/25. 12/4/23- ISD moves to 12/1/27 per QP meeting ​06/16/23- NCW letter and ICC sent to customer ​05/22/23- LIRF deemed complete and customer notified 6/9/22- ISD moves to 12/1/25 per QP meeting 2/26/20- Added to potential queue per QP meeting | Nett, Jason;#1101 | Alternative Assessment | PI155 | N/A | N/A | N/A
2023-04-12 | 2023-05-16 | 40864 | Wisconsin Public Service | Ellisville | New Sub | 36 | 2025-06-01 | WPS is proposing a new T-D interconnection substation with a new 138/24.9 kV, 26/30 MVA distribution transformer with a breaker for high-side protection. ATC will consider constructing a new 0.7 mile double-circuit 138 kV line to loop through a new T-D substation. | ​8/30/23- PM assigned email sent to customer ​06/16/23- CW letter executed ​6/12/23- CW determination sent to customer ​5/16/23- LIRF deemed complete and customer notified 9/29/21- added to potential queue per QP meeting | LeMere, Tim;#827 | Alternative Assessment | 9256 | N/A | N/A | N/A
2023-02-27 | 2023-03-09 | 40341-1 | Wisconsin Public Service | Hodag | Additional Xfmr | 24 | 2025-10-31 | WPS is proposing to install a 2nd 115/24.9 kV, 22 MVA distribution transformer at the Hodag Substation. High-side protection TBD. ATC will consider installing a 138 kV loop through straight bus with provisions for 2 line breakers and a bus-tie breaker. | 12/2/24- per QP meetings, ISD moves to 10/31/25 9/24/24- per QP meeting, ISD moves to 8/31/25 8/5/24- per email from Drew Bain, ISD is pushed out to 12/1/25 on the queue. WPS team is working towards a 8/31/25 ISD with the ATC project team . 8/31/23- PM assigned email sent to customer ​6/1/23- per QP meeting, ISD moves to 6/1/25 ​5/3/23- CW letter executed and returned to ATC ​04/05/23- ICC with CW determination sent to WPS for rev 1 ​3/9/23- LIRF rev 1 deemed complete and customer notified 12/7/22- ISD moves to 12/31/24 per QP meeting 3/9/18- per QP meeting, ISD moves to 2024 09/14/17- Per QP meeting, ISD moves to 6/1/23 09/23/16- moved back to planning queue, ATC planning to begin working on the project 07/18/14- per Planning, move to Inactive queue, project to be reviewed for active status in 2016 06/24/14- LIRF deemed complete and customer notified | Johanek, Dustin;#107 | Alternative Assessment | 9241 | N/A | N/A | N/A
2019-09-17 | 2019-10-01 | 40588 | Wisconsin Public Service | Kelly | Xfmr Repl | 18 | 2025-05-15 | Replacing 115/46 kV Bk 1 transformer with new 56 MVA unit. Replace high-side CS on BK3, 4, 5. | 9/24/24- ISD moves to 5/15/25 due to supply chain issues. 10/5/23- PM assigned email sent to customer 10/1/19- per Norm, ISD is now 12/1/24 10/1/19- LIRF deemed complete and customer notified 6/12/18- ISD moves to 12/1/21 per QP meeting. 06/20/17- added per QP meeting. | Baij, Janssen;#817 | MCW | 9252 | N/A | N/A | N/A
2023-04-12 | 2023-05-01 | 40860 | Wisconsin Public Service | Lost Dauphin | Xfmr Repl | 0 | 2025-06-30 | WPS to replace existing distribution T3 with a new 138/24.9 kV, 26/30 MVA unit. WPS will also replace the high-side switch (399H) and retain the high-side circuit-switcher (399). ATC Scope of Work: Provide new jumpers/insulators to support the new high-side 138 kV disconnect switch. | 9/24/24 - per QP meeting, ISD moves to 6/30/25 3/5/24- ISD moves to 12/31/25 per QP meeting 12/15/23- PM assigned and customer notified ​6/13/23- MCW letter/ICC email sent to customer ​6/1/23- per QP meeting, ISD moves to 12/31/24 ​5/1/23- LIRF deemed complete and customer notified 09/09/20- per QP meeting, ISD moves to 6/1/24 03/09/18- per qp meeting, this project has been added to the potential queue | Baij, Janssen;#817 | MCW | 9270 | N/A | N/A | N/A
2023-05-19 | 2023-06-05 | 40867 | Wisconsin Public Service | Neevin | Additional Xfmr | 24 | 2025-12-01 | WPS is proposing to install a new 138kV/24.9kV, 12/22.4 MVA transformer at the existing Neevin substation. High-side protective device is proposed to be a circuit breaker with a separate high-side switch. ATC will consider extending the Neevin 138 kV bus to add a new terminal position for the proposed WPS distribution transformer addition. | 4/18/24- PM assigned and customer notified 3/11/24- CW letter executed ​6/30/23- ICC email sent to customer with CW determination 06/05/23- LIRF deemed complete and customer notified ​12/7/22 - added to potential queue | Osvatic, Mark;#111 | Alternative Assessment | 9406 | N/A | N/A | N/A
2023-04-26 | 2023-05-23 | 40815-1 | Wisconsin Public Service | Tommys Turnpike (fka Stevens Point Area New Sub) | New Sub | 36 | 2025-12-31 | WPS is proposing a new T-D interconnection substation with 2 new distribution transformers with breakers for high-side protection. ATC will consider installing a 115 kV loop through straight bus with disconnect switches for sectionalizing and provisions for future line and a bus-tie breakers. | 10/26/23- PM assigned and customer notified 9/25/23- PR submitted and pending approval ​6/16/23- CW letter executed ​6/14/23- CW determination sent to customer ​05/23/23- LIRF rev 1 deemed complete and customer notified ​4/12/23- WPS provided new substation name in QP meeting 11/30/22- CW determination and ICC sent to customer 10/31/22- LIRF deemed complete and customer notified 9/29/21- added to potential queue per QP meeting | Baij, Janssen;#817 | Alternative Assessment | 9277 | N/A | N/A | N/A
2020-08-20 | 2020-09-02 | 40645 | Wisconsin Public Service | Wells Street | Xfmr Repl | 36 | 2024-10-01 | WPS to replace 69/12 kV Bank 1 transformers with a new 69/24.9 kV, 22.4 MVA unit. ISD 12/31/2023. ATC to review double circuit J-62 or H-60, and possible reconductor/rebuild of N-14. | 3/4/25- per WPS this project is complete.Kaylin to confirm if Wells St xfmr test report has been received. 9/30/24- ISN received for Wells St SS work, confirm with WPS that this project is completed. 12/4/23- ISD moves to 10/1/24 11/27/23- ISNs received for ATC scope of Marinette Marine load addition 4/12/23- ISD moves to 6/1/24 6/2/21- BVP fully executed and sent to WPS, project has been moved to PM 3/16/21- draft BVP shared with WPS 10/09/20- LIRF ID Corrected and sent to customer 09/09/20 - ICC during QP meeting, see notes 09/02/20- LIRF deemed complete, customer notified 2/26/20- added to potential queue per QP meeting | Hoffmann, Stephan;#129 | Alternative Assessment | 8756 & 8992 | N/A | N/A | N/A
2019-09-03 | 2019-09-16 | 40586 | Wisconsin Public Service | Whiting Ave | Xfmr Repl | 18 | 2025-04-01 | Replace Bank 5&6 with two new115-24.9kV 15MVA (28MVA) units. Replace Bank 4,5,6 circuit switchers w/ Series 2000. ATC new jumpers and insulators to Bank 4,5,6. | 12/2/24- per QP meetings, ISD moves to 04/01/25 7/24/24- ISD moves to 2/28/25 per WEC North QP meeting 10/05/23- PM assigned and customer notified ​6/15/23- MCW letter sent to customer 12/12/22- WPS provided email with updated scope -xfmr size updated 7/24/20- per email from Norm, ISD is 12/1/24 9/16/19- LIRF deemed complete and customer notified 6/12/18- per QP meeting, ISD moves to 12/1/22. 06/20/17- added per QP meeting | Baij, Janssen;#817 | MCW | 9253 | N/A | N/A | N/A
2023-01-25 | 2023-02-08 | 40843 | Wisconsin Rapids Waterworks ＆ Lighting | Northern Casting Steel | Retirement |  | 2024-10-01 | ​WWLC is requesting retirement of the Northern Steel Casting Substation. This facility burnt down about 5 years ago and was never rebuilt. ATC Scope of Work: ATC will investigate what transmission facilities that need to be retired. | 10/24- PM reassigned -Paula Hammersly - Contract PM with oversight from Bobby Lamphsire 2/5/24- ISN received for the tap retirement 1/8/24- ISD moves to 10/1/24 per discussion with regional manager. ​ 8/30/23- PM assigned email sent to customer ​3/6/23- MCW letter sent to customer ​2/8/23- LIRF deemed complete and customer notified | Lampshire, Robert;#112;#Hammersley, Paula;#960 | MCW | 9199 | N/A | N/A | N/A

## NCW
2025-04-01
ISD has passed
ISD is within 90 days of Queue posting
LIRF/DERRF Received | LIRF/DERRF Complete | LIRF/DERRF ID # | Distribution Customer | Project Name | Project Type | Estimated ATC Project Lead-Time After PCA Execution | Requested In-Service Date | Projected Scope of Work | Notes & Updates | CPS Coordinator | ATC Commissioning Engineer | ATC System Protection Engineer | BVP Type
2025-01-13 | 2025-01-15 | 41078 | Alliant Energy | 20th St | Sub Rebuild | 0 | 2026-12-31 | WPL to replace aging recloser distribution bay with 6-feeder switchgear. WPL to retain existing high side breaker and transformer, retire transformer controls from ATC control house and use standard control package in new switchgear building.ATC Scope - None | 2/12/25- NCW letter sent to customer 01/15/25- LIRF deemed complete and customer notified | Glauser, Chris | Malter, Kevin |  | NCW - LDC Support
2024-07-23 | 2024-08-05 | 41017 | Alliant Energy | Arnott | Sub Rebuild | 18 | 2026-12-30 | WPL is replacing their 12kV bus, transformer and high side protection. The site will also be expanded for additional equipment. ATC to install jumpers and insulators to the new high side protective device. ATC to retire existing jumpers and insulators on the box structure. | 10/21/24- NCW letter sent to customer based on discussions with WPL 9/3/24- MCW letter sent to customer 8/5/24- LIRF deemed complete and customer notified | Glauser, Chris |  |  | NCW - LDC Only
2023-09-20 | 2023-10-05 | 40897 | Alliant Energy | McFarland (McFarland School) DER | Distributed Energy Resource | 0 | 2025-08-01 | Alliant to install 1.4MW of solar DER as part of their customer hosted program. They plan to connect this array to a distribution feeder off bus #1 at the McFarland Substation. No ATC scope of work; all surge arrestors are either upgraded to 106kV MCOV or will be as part of another solar project (17.32MW @ Dane County Landfill – PR08813) at the McFarland substation. | 3/6/25- ISD moves to 8/1/25 per QP meeting. 9/27/24- ISD moves to 6/30/25 2/28/24/ - ISD moved to end of December 2024 per feedback from quarterly Planning meeting.10/26/23- NCW letter and ICC email sent to customer 10/05/23- DERRF deemed complete and customer notified | Glauser, Chris |  |  | NCW - LDC Only
2024-09-19 | 2024-09-27 | 41038 | Alliant Energy | Portage | Xfmr Repl | 0 | 2028-12-31 | WPL is replacing their existing transformer with a 138/25-12.47kV 33 MVA rated transformer. WPL is replacing the high-side 138 kV circuit switcher with a 138 kV breaker. Connecting to existing insulators. ATC Scope of Work: No Capital Work - LDC Support | 10/29/24- NCW letter and email sent to customer 9/27/24- LIRF deemed complete and customer notified | Glauser, Chris |  |  | NCW - LDC Only
2023-06-01 | 2023-06-14 | 40872 | Alliant Energy | Rock River (Rock Road) DER | Distributed Energy Resource | 18 | 2025-12-01 | Alliant will construct 1.2 MW of customer-hosted Solar DER. 1.2 MW solar DER will feed into the new Rock River 138/12.47 kV, 20/33 MVA transformer. ATC scope of work: No Capital Work (LDC-only) due to three transmission outlets from Rock River 138 kV Bus 3 (TLR 138 kV Line X-73, JAN 138 kV Line X-24, Rock River 138 kV Bus 2/3 tie breaker 530-S). | 2/28/24- ISD moved to 12/1/25 per quarterly planning meeting.​7/13/23- ICC email with NCW determination sent to WPL ​06/14/23- DERRF deemed complete and customer notified | Glauser, Chris |  |  | NCW - LDC Only
2008-11-26 | 2008-12-09 | 40095-1 | Alliant Energy | South Monroe | Sub Rebuild | 12 | 2026-12-01 | NCW | 8/16/22- ISD moves to 12/1/26 1/31/22- per update at QP meeting, ISD moves to 12/1/25 9/15/21- ISD moves from 12/1/23 to 12/1/24 3/25/20- per QP meeting, ISD moves to 12/1/23 10/9/19- per QP meeting, ISD is TBD. Moved to 12/1/25 for tracking purposes. 09/11/17- per QP meeting, ISD moves to 12/1/22 12/8/16- per Greg's email, ISD is now 12/1/20 08/08/16- per Greg via email, ISD moves from 12/31/18 to 12/1/19 04/27/16- per QP meeting, ISD moves from 2019 to 2018 02/23/16- per email from Alliant, ISD moves from 6/1/19 to 12/31/19 4/15/14- per QP meeting, ISD moves from 16 to 19 11/12/11 e-mail changing ISD from 15 to 16 | Glauser, Chris |  |  | NCW - LDC Support
2024-11-07 | 2024-11-19 | 41056 | Alliant Energy | Spring Green (River Run Solar) | Distributed Energy Resource | 0 | 2027-12-31 | A third party developer to install a new 5 MW solar with 4.9 MW battery storage facility. The total power export will be restricted to 4.9 MW. WPL to perform the interconnection to the Spring Green distribution transformer XF2. No ATC scope of work; 3x network sources. | 12/16/24- NCW letter sent to customer 11/19/24- DERRF deemed complete and customer notified | Glauser, Chris |  |  | NCW - LDC Only
2023-01-03 | 2023-01-17 | 40839 | Alliant Energy | Vienna (Walbec Vienna) DER | Distributed Energy Resource | 18 | 2025-12-31 | Sunvest will be constructing 1.4 MW of solar DER and transferring ownership to Alliant. Alliant will interconnect the 1.4 MW of solar DER to a Vienna substation feeder (VIEN14817) and may connect to the ATC system through the existing VIE T31 138/12.4 kV, 15/20/25 MVA transformer. ATC scope of work: No Capital Work | 3/6/25- ISD moves to12/31/25 per QP meeting. 12/12/24- revised BVP doc sent to WPL. This is now NCW as the WPL DER at American was placed in-service first. NCW letter sent. 9/27/24-per update at QP meeting, ISD moves to 6/30/25 ​2/7/23- MCW letter and ICC sent to customer ​1/17/23- DERRF deemed complete and customer notified | Glauser, Chris |  |  | NCW - LDC Only
2025-02-24 | 2025-02-24 | 41088 | Cloverland Electric Cooperative | Trout Lake | Load Addition | 0 | 2025-06-01 | Cloverland to tap existing distribution network to serve load addition at Trout Lake. ATC Scope of Work: The scope of work identified in the CEC Trout Lake LIRF only involves distribution upgrades, however it needs to be confirmed whether ATC system upgrades are needed to support this load addition. Capital Work Status to be determined, lead time to be determined | 3/25/25- NCW letter sent to customer 2/24/25- LIRF deemed complete and customer notified | Glauser, Chris |  |  | TBD
2025-02-20 | 2025-02-26 | 41091 | Madison Gas ＆ Electric | Nine Springs (Murphy Creek) DER | Distributed Energy Resource | 0 | 2027-09-01 | MGE to install a new solar facility near the Nine Springs substation. The facility capacity is still preliminary, but it is currently rated at 7.5 MW. MGE plans to connect the new DER to the Nine Springs distribution transformer T1. No ATC scope of work. Required surge arrester upgrades are included in an existing project (Syene SS DIC – PR09375). | 3/26/25- NCW letter sent to customer 3/18/25- ISD moves to 9/1/27 per update from MGE 3/6/25- per guidance from MISO, DER AFS study is not required for this project (see email in records). 2/26/25- DERRF deemed complete and customer notified | Glauser, Chris |  |  | NCW - LDC Only
2023-08-04 | 2023-08-18 | 40868-1 | Manitowoc Public Utilities | Custer (MPU Community Garden Solar) | Distributed Energy Resource | 0 | 2024-06-01 | Manitowoc Public Utilities installing 1.5 MW of solar DER connected to the Custer T2 (13.8 kV bus). ATC Scope - NCW – LDC only: Custer has 3 network lines, preliminary assessment is no protection or insulation coordination required. | 1/11/24- per update from David England at MPU, ISD moves to 6/1/24 ​8/18/23- DERRF rev1 deemed complete 7/5/23- NCW letter and ICC email sent to customer ​6/7/23- DERRF deemed complete and customer notified | Glauser, Chris |  |  | NCW - LDC Only
2024-06-24 | 2024-07-02 | 40999 | Mount Horeb Utilities | Wally Road | Xfmr Repl | 0 | 2025-02-01 | Mt Horeb Utilities is planning to replace the transformer at their Wally Road substation with a new 10/14 MVA transformer with a larger capacity for serving load. No ATC work scope anticipated. | 3/24/25- per Forster meeting, this project is complete. Confirm if xfmr test report has been received. 12/17/24 Active construction for bank replacement ongoing, moved IDS to 2/1/25 7/23/24- NCW letter sent to customer 7/2/24- LIRF deemed complete and customer notified | Glauser, Chris |  |  | NCW - LDC Only
2020-04-16 | 2020-04-27 | 40624 | Upper Peninsula Power Company | Keweenaw | Other Substation Equipment Modification | 6 | 2025-12-31 | UPPCO to replace existing 69-kV fuse with circuit switcher or circuit breaker. ATC to provide protection and commissioning support. High-side disconnect switch will remain the same. | 10/2/24- per QP meeting, ISD moves to 12/31/25 5/7/24 - Update from quarterly planning meeting is that his work has moved up to end of 2025, changed ISD to 11/14/25 5/9/22 Per QP meeting ISD updated 10/26/21- ISD moves from 2022 to 2025, per UPPCO QP meeting 4/22/21- NCW letter sent to customer 4/27/20- LIRF deemed complete and customer notified. Previous LIRF #40501 has been cancelled. | Glauser, Chris |  | Pynenberg, Randy | NCW - LDC Support
2020-10-15 | 2020-10-23 | 40224-2 | Upper Peninsula Power Company | M-38 | Additional Xfmr | 42 | 2025-10-15 | UPPCO to add a 138/12.47 kV, 7 MVA unit. UPPCO to utilize 138 kV 2619A bus switch as interconnection point. Fuse as high-side protection. Secondary to be fed underground to spare 12 kV feeder position, and UPPCo to replace 745 recloser with circuit breaker. | 12/14/23- ISD updated to 10/15/2025 via email from Dan Gervae. Shared with Adam Brecklin (CPS coordinator). ​4/19/23- NCW letter sent to customer 10/21/22- update provided by UPPCO, ISD is 12/1/25. ATC will need to cancel current PR and submit new PR for expanded scope. 5/9/22 Per QP meeting ISD updated 11/16/20- initial customer communication sent to customer 10/23/20- LIRF rev 2 deemed complete and customer notified 4/15/20- per QP meeting, ISD moves to 12/1/24 2/20/20- per email with Tim, ISD is 12/1/25 5/2/19- per UPPCO Capital Plan, ISD is TBD 4/15/19- per QP meeting, ISD moves to 10/1/22 2/25/19- PM assigned and customer notified 2/20/19- CW letter executed and saved to IRM 10/20/17- per QP and UPPCO capital plan, ISD moves to 2020. 03/30/17- LIRF revision deemed complete and customer notified 10/14/16- per UPPCO Capital Plan, ISD moves to 2020 07/10/13 per UPPCO, on hold 12/22/11 informed UPPCO that LIRF is Complete: on Potential queue because of the 2019 ISD; Construction Lead Time: 2 years, Planning Lead time: 6 months, Start Date: June 2016 | Glauser, Chris | Muller, Jill | Sessler, Greg | NCW - LDC Support
2023-05-15 | 2023-05-31 | 40866 | Upper Peninsula Power Company | MTU Bank 1 | Xfmr Repl | 12 | 2024-11-22 | UPPCO will replace the Bank 1 transformer with 69/12.47 kV, 14 MVA base transformer. UPPCO will also replace the existing 847 fuses with a high-side 69 kV breaker. Undetermined on whether the 840 switches will be replaced (one-line diagram pending). ATC Scope - NCW, Minor Atlantic HOUGHTON line relaying modifications | 9/16/23 - Notified ISD pushed back to mid to late November, move ISD to 11/22.​6/28/23- NCW letter sent to UPPCO/ICC email ​5/31/23- LIRF deemed complete and customer notified ​5/15/23- ISD updated to 10/1/24, LIRF submitted that day via email. 5/9/22 Per QP meeting ISD updated to 6/1/2024 10/26/21- scope updated during QP meeting 9/24/19- per QP meeting, ISD moves to 6/1/23 4/17/18- added per UPPCO capital plan at QP meeting. | Glauser, Chris | Muller, Jill | Parker, Derek | NCW - LDC Support
2024-04-24 | 2024-05-03 | 40974 | Upper Peninsula Power Company | MTU Load Addition | Load Addition | 0 | 2025-05-01 | UPPCO submitted this LIRF for a 1.129 MW load addition at MTU substation. This is related to improvements/development (dormitories) at the Michigan Tech University Campus. For the 1.1 MW load addition, this is a No Capital Work – LDC only | 5/31/24- NCW letter and ICC email sent to customer 5/3/24- LIRF deemed complete and customer notified | Glauser, Chris |  |  | NCW - LDC Only
2023-12-04 | 2023-12-19 | 40935 | Upper Peninsula Power Company | Osceola | Load Addition | 0 | 2025-06-01 | Third party customer is planning an operational expansion that will result in an additional 1.9MW of load. The added load will be on UPPCO’s Osceola substation. The necessary distribution upgrades to support the load are still being determined. No ATC scope of work assumed at this time. The proposed load is relatively small and the existing system seems like it can support the load. This will be further reviewed with Michael Billups for confirmation. | 10/2/24- per update at QP meeting, load addition of 3.2 MWs is reduced to 1.9 MWs. 1/19/23- NCW letter sent to customer 12/19/23- LIRF deemed complete and customer notified | Glauser, Chris |  |  | NCW - LDC Only
2024-06-25 | 2024-07-08 | 41001 | We Energies | O'Connor | Xfmr Repl | 0 | 2025-05-01 | We Energies is planning on replacing transformer T6 at their O’Connor Substation with a new, higher capacity 138kV – 13.8Y/7.97 kV, 30/40/50 MVA transformer. We Energies will also install a new 3000 amp bus duct to make up for offsets in all three directions and to allow for easier future modifications. The primary driver for this project is the condition and age of the existing transformer. No ATC work scope anticipated, but CPS support is needed. | 12/4/24- ISD moves to 5/1/25 9/3/24 - Notified by WEC that the ISD for this has pushed out to 3/31/25. No ATC print review needed. Reclassify to NCW - LDC Only. 7/23/24- NCW letter sent to customer. CPS will be needed to coordinate outages and commissioning/system protection work. 7/8/24- LIRF deemed complete and customer notified | Glauser, Chris |  |  | NCW - LDC Only
2022-07-01 | 2022-07-15 | 40798 | We Energies | Root River | Xfmr Repl | 18 | 2026-02-01 | ​WEC to replace both distribution transformers (T7 and T8) with new 138/24.9 kV, 42/56/70 MVA units. ATC Scope: No breakers need, likely NCW – LDC Only. | 3/5/25- per QP meeting, ISD moves to 2/1/26 12/4/24- ISD moves up to 12/31/26 3/12/24 - WE notified that replacement is no longer part of 2025 work plan, likely out a few years. New tentative ISD is 12/1/27. ​8/10/22- NCW letter sent to customer 7/15/22- LIRF deemed complete and customer notified | Glauser, Chris |  |  | NCW - LDC Only
2024-02-14 | 2024-02-26 | 40955 | We Energies | St Martins | Xfmr Repl | 0 | 2025-11-30 | WEC is proposing to replace T1 and T2 transformers with new 138kV/26.2kV, 50.4/67.2/84 MVA transformers at the existing St Martins substation. WECverified existing high side protection will be retained. ATC Scope of Work: No Capital Work | 6/5/24 - Update from Tiffany Goebel, new projected ISD for these units is November 25, moving ISD to 11/30/25. 4/19/24 - Got notice from WE that the transformers for St. Martins got moved to a different project, and this work is no longer in the 2024 workplan. Changed ISD to end of 2024 until ATC gets an updated ISD for this work.3/26/24- NCW letter sent to customer 2/26/24- LIRF deemed complete and customer notified | Glauser, Chris |  |  | NCW - LDC Support
2023-02-27 | 2023-03-13 | 40850 | We Energies | St Rita Cap Bank Removal | Retirement |  | 2025-06-01 | ​WEC is requesting to retire the St. Rita distribution cap bank. ATC to determine if a system study is needed. NCW, if retirement has no transmission system impacts | 3/13/24- ISD updated to 6/1/25 at QP meeting ​06/08/23- per QP meeting, ISD moves to 4/30/24 ​4/10/23- NCW and ICC email sent to customer ​3/13/23- LIRF deemed complete and customer notified | Glauser, Chris |  |  | NCW - LDC Only
2023-05-31 | 2023-06-13 | 40869 | Wisconsin Public Service | Pearl Ave | Xfmr Repl | 0 | 2028-12-01 | WPS will replace the Bank 1 and 2 transformers with 69/24.9 kV, 15 MVA base transformer. Existing high side switches/protection to be retained. No ATC capital work anticipated. Verified no high-side work to be completed with WPS. | ​​​8/23/23- per update from Logan P, ISD moves to 12/1/28 ​07/11/23- NCW letter and ICC sent to customer ​06/13/23- LIRF deemed complete and customer notified 6/9/22- ISD moves to 12/1/26 per QP meeting 2/26/20- added to potential queue per QP meeting | Glauser, Chris |  |  | NCW - LDC Only

## In-active
2025-04-01
ISD has passed
ISD is within 90 days of Queue posting
LIRF/DERRF Received | LIRF/DERRF Complete | LIRF/DERRF ID # | Distribution Customer | Project Name | Project Type | Estimated ATC Project Lead-Time After PCA Execution | Requested In-Service Date | Projected Scope of Work | Notes & Updates | ATC Project Manager | BVP Type | PR # | PCA # | Construction PCA Sent | Construction PCA Signed
2022-06-29 | 2022-07-13 | 40796 | Alliant Energy | Albany Reimer Solar (Albany) | Distributed Energy Resource | 9 | 2025-12-01 | ​5 MW solar DER will feed into the Albany 25 kV bus. ATC will consider conducting insulation/protection coordination and upgrade the arresters at North Monroe and Bass Creek Substations from line X-12. | 9/27/24- ISD moves to 2025 per QP meeting ​04/05/23- move to in-active queue per Alliant QP discussion ​2/28/23- MCW letter sent to customer ​7/13/22- DERRF deemed complete and customer notified |  | MCW |  | ​N/A | ​N/A | ​N/A
2021-11-08 | 2021-11-19 | 40738 | Alliant Energy | Apex Oregon Solar | Distributed Energy Resource | 9 | 2025-12-01 | 5 MW solar DER addition will feed into transformer T41 at the Sun Valley Substation. ATC scope of work: Insulation/protection coordination from Verona to Oregon (Y-119). | 9/27/24- ISD moves to 2025 per QP meeting 3/14/24- ISN received for ATC scope 2/28/24- remains inactive. Approved to push ISD into 2024 ​2/22/23- per update from Alliant and ATC PM, this project is currently on hold. ​1/17/23- PM assigned email sent to customer, will be coordinated with the Oregon xfmr replacement project 12/13/21- ICC and MCW letter sent to customer 11/19/21- DERRF deemed complete and customer notified | Mainwaring, Kyle;#119 | MCW | 9150 | ​N/A | ​N/A | ​N/A
2024-11-11 | 2024-11-21 | 41058 | Alliant Energy | Belleville (BlueWave Solar) | Distributed Energy Resource | 12 | 2026-12-29 | A third party developer to install a new 4.98 MW solar DER facility. WPL to perform the interconnection to the Belleville transformer #1. ATC to upgrade the following surge arresters to 57kV MCOV to support the project: On line Y-208 (Verona – Belleville – New Glarus) Verona and New Glarus terminals On line Y-42 (New Glarus – North Monroe) both terminals Surge arresters are not currently installed at Belleville, but if they will be installed as part of Belleville SS, DIC, Substation Rebuild (PR09170, WO# 605827) then they should be upgraded to 57kV MCOV. | 3/6/25- placed on inactive/on hold status 12/18/24- MCW letter sent to customer 11/21/24- DERRF deemed complete and customer notified |  | MCW |  | ​N/A | ​N/A | ​N/A
2022-06-29 | 2022-07-13 | 40797 | Alliant Energy | Blacksmith (Garrison Twin Grove Solar) | Distributed Energy Resource | 9 | 2025-12-01 | 5 MW solar DER will feed into the Blacksmith T41 transformer. ATC will consider conducting insulation/protection coordination and upgrade the arresters at South Monroe and Broadhead Substations from line Y-33. | 9/27/24- ISD moves to 2025 per QP meeting ​6/6/23- moved to inactive on hold per Alliant ​12/21/22- MCW letter sent to customer 7/13/22- DERRF deemed complete and customer notified |  | MCW |  | ​N/A | ​N/A | ​N/A
2023-10-16 | 2023-10-31 | 40914 | Alliant Energy | Browntown (Browntown Grede CH) Solar | Distributed Energy Resource | 12 | 2025-01-30 | Alliant to install a new 1.5MW solar DER facility at the Grede Foundry (Browntown) as part of their customer hosted program. Alliant to connect the facility on the distribution side of the Browntown substation. This will be done after the sub rebuild project (LIRF 40517, PR08539) is complete per the DERRF. ATC to consider upgrading the following surge arrestors as part of the project. The existing surge arrestor values are note listed in Cascade and so an upgrade was assumed: Y-155 South Monroe Terminal Y-155 Jennings Rd. Terminal Shunt Capacitor Bank C1 (6207-CS) at South Monroe Shunt Capacitor Bank C2 (6208-CS) at South Monroe | 11/27/24- move to inactive per Bob Grabow 11/30/23- MCW letter and ICC sent to customer 10/31/23- DERRF deemed complete and customer notified |  | MCW |  | ​N/A | ​N/A | ​N/A
2024-07-26 | 2024-08-08 | 41019 | Alliant Energy | Huebner | 3rd Xfmr | 24 | 2027-12-31 | Alliant is planning to add a third transformer to the Huebner substation, with an open-air bus or switchgear design depending on available space. ATC Scope of Work: Relocate cap bank and breaker on the west side of the station. Add bus supports and connection to new Alliant transformer. Install 1 bus tie breaker and 2 line breakers. | 11/14/24- per update from Alliant, this project is on hold as Alliant looks at the surrounding area, Alliant’s long-term needs and what other projects they might identify. 9/12/24- ICC email with capital work determination sent to customer. CW letter to follow at later date. 8/8/24- LIRF deemed complete and customer notified |  | Alternative Assessment |  | ​N/A | ​N/A | ​N/A
2023-09-26 | 2023-10-11 | 40901 | Alliant Energy | Idle Hour (Green County DER) | Distributed Energy Resource | 12 | 2027-12-01 | Alliant is reviewing an application to install an additional 1MW of solar DER at the Idle Hour (IDH) substation. Based on the DER it sounds like this is a preliminary review and isn’t clear on whether this will be Alliant or third party owned. If the DER goes through, Alliant to perform the connection to the Idle Hour substation. ATC to consider upgrading the surge arrestors on the North Monroe & South Monroe terminals of Y-87. Both terminals do not have their current ratings listed on Cascade and should be upgraded if they aren’t already. As such we’ll assume they need to be for now. | 11/27/24- move to inactive per Bob Grabow 11/9/23- MCW letter and ICC email sent to customer 10/11/23- DERRF deemed complete and customer notified |  | MCW |  | ​N/A | ​N/A | ​N/A
2013-12-04 | 2013-12-13 | 40317 | Alliant Energy | Rosholt | Xfmr Repl | 18 | 2027-06-01 | Install temporary facilities at Rosholt Substation to accommodate the transformer replacement | 09/11/17- per QP meeting, ISD moves to 6/1/27 04/4/17- per QP meeting, move to on hold queue. Sub is likely to retire 04/27/16- per QP meeting, ISD moves from 5/1/16 to 5/1/18 01/30/15- per new Alliant schedule, ISD moves from 5/1/15 to 5/1/16 4/7/14- per RM, PCA will not be needed, will most likely by MCW. Customer notified of PM assignment. 3/31/14- PR is approved and PM has been assigned 3/14/14- Per M.Waldron, PR is submitted and awaiting PM assignment 1/21/14- Alliant to determine if mobile SS is needed, if mobile SS is needed project will be NCW; waiting for reply from Alliant 12/17/13 ATC informed Alliant that LIRF rev. 0 is complete | Osvatic, Mark;#111 | MCW | 6351 | ​N/A | ​N/A | ​N/A
2022-06-29 | 2022-07-13 | 40795 | Alliant Energy | Southwest Delevan (East Darien Solar) | Distributed Energy Resource | 9 | 2025-12-01 | ​​ 5 MW solar DER will feed into the Southwest Delevan transformer T31. ATC scope - no capital work | 9/27/24- ISD moves to 2025 per QP meeting 4/5/23- moved to inactive queue per Alliant QP meeting ​​12/21/22- NCW letter sent to customer 7/13/22- DERRF deemed complete and customer notified | Brecklin, Adam;#732 | NCW - LDC Only |  | ​N/A | ​N/A | ​N/A
2022-06-22 | 2022-07-06 | 40791 | Alliant Energy | Trinity School Solar (Howards Grove) | Distributed Energy Resource | 3 | 2025-12-01 | ​5 MW solar DER will feed into the Howards Grove T81 Transformer. ATC scope of work: No Capital Work. | 9/27/24- ISD moves to 2025 per QP meeting 2/28/24- remains inactive. Approved to push ISD into 2024 4/5/23- moved to inactive queue per Alliant QP meeting ​​8/1/22- ICC and NCW letter sent to customer 7/6/22- DERRF deemed complete and customer notified | Rawson, Christine;#101 | NCW - LDC Only |  | ​N/A | ​N/A | ​N/A
2020-07-07 | 2020-07-21 | 40638 | Alliant Energy | Vir Clar Farms | Distributed Energy Resource | 9 | 2024-12-31 | Private Customer 1 MW Solar DCG. ISD 1/20/2021. 1 MW Solar DCG addition will feed into Martin Road Xfmr T31. ATC scope of work: Insulation/protection coordination from Ohmstead to South Fond du Lac 138 kV (X-25). | 12/9/24- per WPL, this DER project moves to inactive/on hold 9/26/23- ISD moves to 12/31/24 per QP discussion 8/16/22- ISD moves to 12/31/23 1/31/22- ISD moves to 12/31/22 per QP meeting 9/15/21- ISD moves from 8/31/21 to 12/31/21 6/15/21- per QP meeting, ISD moves to 08/31/21 3/9/21- per QP meeting, ISD moves to 6/30/21 1/28/21- ISN for ATC work received, Jim Z to confirm WPL completion 8/25/20- PM assigned and customer notified 8/17/20 - ICC and MCW letter sent to customer 07/21/20- LIRF deemed complete and customer notified. | Meiers, Jon;#514 | MCW | 8656 | ​N/A | ​N/A | ​N/A
2022-06-29 | 2022-07-13 | 40794 | Alliant Energy | West Darien - Turtle Creek Solar | Distributed Energy Resource | 9 | 2025-12-01 | ​5 MW solar DER will feed into the West Darien T31 transformer. ATC will consider conducting insulation/protection coordination and upgrade the arresters at Rock River and Southwest Darien from line X-79. | 9/27/24- ISD moves to 2025 per QP meeting ​04/05/23- move to in-active queue per Alliant QP discussion ​​12/21/22- MCW letter sent to customer 7/13/22- DERRF deemed complete and customer notified |  | MCW |  | ​N/A | ​N/A | ​N/A
2024-01-24 | 2024-02-06 | 40952 | Alliant Energy | Wolf (Polka King 16) DER | Distributed Energy Resource | 12 | 2025-12-31 | A third-party developer to install a new 5MW solar DER facility. WPL to connect the new DER to the distribution side of Wolf transformer T31. ATC to upgrade the following surge arrestors to 106kV MCOV to support the proposed DER: Line 85851 (West Shawano - East Shawano) terminals Line 26523 (White Clay – East Shawano) terminals Line 86504 (Badger – West Shawano) terminals Badger C5 Cap Bank (C5) terminal | 2/29/24- MCW letter sent to customer 2/28/24- per QP discussion, move to inactive queue 2/14/24- initial scope sent to WPL (for regulatory filing deadlines). MCW letter to follow. 2/6/24- DERRF deemed complete and customer notified |  | MCW |  | ​N/A | ​N/A | ​N/A
2016-08-22 | 2016-08-25 | 40229-1 | Upper Peninsula Power Company | Chatham | Xfmr Repl | 24 | 2026-12-31 | change to Bk1 Transformer Replacem | 10/2/24- on hold per update from UPPCO at QP meeting. 10/5/22- per QP meeting, ISD moves to 12/31/26 5/9/22 Per QP meeting scope updated 2/1/21- per UPPCO, ISD moves to 12/31/24 4/15/20 - per QP meeting, ISD moves to 12/31/23 9/24/19- Per UPPCO capital plan, ISD moves to 12/31/22 4/15/19- per QP meeting, ISD moves to 6/1/22 10/20/17- per QP meeting, ISD moves to 2021 4/4/17- per QP meeting, ISD is 6/1/19 08/25/16- LIRF revision deemed complete and customer notified 07/10/13 per UPPCO, on hold 01/05/12 informed UPPCo LIRF is complete |  | Alternative Assessment |  | ​N/A | ​N/A | ​N/A

## Definitions
Queue Column Heading | Definition
Action Items | What may be needed for the LIRF/DERRF to be deemed complete, the BVP process to commence or complete, the PCA process to commence or complete, or involve construction of the project. It is meant to denote what is needed for the project to move forward.
Agreement Sent Date | Date a final PCA is sent to the Customer for signature. Enter “N/A” if a PCA is not required (esp. for legacy projects) and for No Capital Work projects.
Agreement Signed Date | Date the PCA is signed by the last party. For Network Projects this would be the date our customer signs the agreement, for regular and end use projects it would be the date ATC signs the agreement. Enter “N/A” if a PCA is not required (esp. for legacy projects) and for No Capital Work projects.
ATC Planner | ATC planner responsible for the project.
BVP (Best Value Plan) Levels | No Capital Work (LDC Only or LDC Support) - No ATC Capital Work and no transmission analysis
Minimal Capital Work - Minor amount of ATC infrastructure to be installed. Minimal ATC Capital Work and no transmission analysis
Alternative Assessment - May include a transmission alternatives for interconnecting the load to the transmission system or assessment of multiple substation configurations. Potential for planning analysis of alternatives including a difference analysis (compared to the base case model) and possibly different transmission system network and load configurations – amount determined by engineering judgment and team meetings
System Study - Transmission Analysis - Modeling analysis for at least two alternatives including a difference analysis (compared to the base case model) including NERC TPL contingencies with different transmission system network and load configurations. Modeling will encompass at least a 10 year planning horizon
System Study and PSCW Filing - ATC needs to file a Certificate of Authority (CA) or Certificate of Public Convenience and Necessity (CPCN) with the PSCW
CPCN Requirements: > 1 mile of new ROW, ≥115 kV; 30 months lead time for CPCN process, 54 months total project
Distribution Customer | The Company that submitted the LIRF or DERRF.
Distribution Customer Contact | Customer contact for the project.
E.D. = Economic Development | Mark Y or N to tell if the project is due un-forecasted load or not
Estimated ATC Project Lead-Time after PCA Execution | The amount of time (in months) that ATC requires to complete its Projected Scope of Work after receiving a customer signed PCA. In the earliest stages of project planning and until ATC can define any specific scope for work, the following default leadtimes will apply based upon Project Type: New Substation: 54 months Load Addition, Loop thru bus, Loop thru bus w/ breaker, Substation Rebuild, Additional Transformer, Other: 24 months Retirement, Distribution Connected Generation, Replacement Transformer: 18 months No Capital Work: 0 months
LIRF/DERRF Complete | The date that ATC deemed the LIRF or DERRF complete.
LIRF/DERRF ID No. | Sequential number given to each submitted LIRF or DERRF. (5 digit number - revision number, example 40000-1)
LIRF/DERRF Received | The date the Customer submitted a Load Interconnection Request Form (LIRF) or DER Request Form (DERRF) to ATC. An email notification is sent to the customer once the LIRF/DERRF has been deemed complete by ATC's Planning department.
Notes & Updates | Anything that is essential to properly considering the project schedule and/or progress. Can be used in facilitating meetings with the customer.
Notification Type | How ATC was notified of the project. Examples include, Quarterly Planning Meetings, public announcements, project meetings… (Potential Projects).
PCA No. | The number assigned to a Project Commitment Agreement (PCA) between ATC and the customer. The number (XXXX-X) represents the year the agreement was signed in followed by a dash and the total number of agreement signed up to the date of the new agreement. If an amendment to a PCA occurs the number length will extend to XXXX-X-X. All numbers are assigned by ATC's Interconnection Services Administrator.
PR No. | The identification number assigned to an approved project request (PRF). This process allocates dollars to the project.
Project Manager | ATC’s project manager responsible for implementing ATC’s engineering and construction portion of the project after a PRF is approved. Responsible for the development and execution of a Project Commitment Agreement (PCA), if one is necessary.
Project Name | As represented by the Customer on the LIRF, the name of the substation (new or existing) at which the load interconnection addition or change will take place.
Project Notification Date | The date ATC was notified of a potential project. (Potential Projects).
Project Type | General descriptions summarizing the Customer's scope of work.
Projected Scope of Work | A description of ATC's scope of work as best known at any given point in the development or implementation of the project. It should include a summary of key configuration elements and any related network reinforcements.
Requested In-Service Date | The in-service date most recently approved by the customer as representing their present needs. "TBD" indicates a date has not yet been determined.