## Planning
2026-04-08
ISD has passed
ISD is within 90 days of Queue posting
LIRF/DERRF Received | LIRF/DERRF Complete | LIRF/DERRF ID # | Distribution Customer | Project Name | Project Type | Estimated ATC Project Lead-Time After PCA Execution | Requested In-Service Date | Projected Scope of Work | Notes & Updates | ATC Planner | BVP Type
2025-10-31 | 2025-11-14 | 41186 | Adams Columbia Electric Cooperative | Columbus South | Additional Xfmr | 12 | 2029-01-01 | ACEC to install an additional 7 MVA, 69 kV to 12.47 kV transformer at the Columbus South Substation, 69 kV switch, 69 kV circuit switcher, low side switchgear with 4 feeder bays, and transfer the ACEC Columbus South customer load to the new transformer. The proposed ATC bus reconfiguration is planned to be constructed as part of the Columbus Reconfiguration Project (PI144). ATC to install jumpers or rigid bus extension from the ATC 69 kV bus to the new ACEC 69 kV switch. | 1/23/26- MCW letter sent to customer 11/14/25- LIRF deemed complete and customer notified | McGowan, Gavin | MCW
2025-10-03 | 2025-10-22 | 41178 | Adams Columbia Electric Cooperative | Friesland (Aslum Farms) DER | Distributed Energy Resource | 12 | 2026-12-31 | A third-party developer to install a new 1.0 MW solar facility. ACEC to connect the new facility to the distribution side of the Friesland transformer T31.To support the DER addition, ATC will upgrade transmission system surge arresters as needed on nearby lines. This includes arresters on line X-98 (North Randolph - Staff) both North Randolph and Staff terminals, Line SFFG11 (Staff -Glacier Hill) Staff terminal, and Line X-6 (Portage - Staff) Staff terminal | 2/20/26- per update from customer, ISD moves to 12/31/26. DER developer is waiting on materials. 11/12/25- MCW letter sent to customer 10/22/25- initial MCW email sent to customer. MCW letter to follow after cross functional review. 10/22/25- DERRF deemed complete and customer notified | Pirkola, Logan | MCW
2025-09-18 | 2025-10-02 | 41174 | Alliant Energy | Arena | Xfmr Repl | 18 | 2028-12-31 | WPL to rebuild the Arena substation with a 10/12.5 MVA transformer, high and low side circuit breakers, and standard WPL protection package. Plan for an open-air distribution bus with three feeders initially. ATC to replace single span from structure 118652 to new WPL dead-end (DE) structure. Structure 118652 to remain in place.ATC to coordinate portable sub connection between structure 118544 and 118545. | 12/9/25: Per QP Meeting, switching this project off of Confidential 10/29/25 – MCW letter sent 10/2/25 – LIRF deemed complete, customer notified 03/13/19- ISD moves to from 2022 to 2028 09/11/17- ISD moves to 6/1/22 01/30/15- Alliant schedule changes ISD from 2020 to 2021 | McGowan, Gavin | MCW
2023-09-13 | 2023-09-27 | 40895 | Alliant Energy | Baraboo | Xfmr Repl | 18 | 2028-12-01 | Alliant to rebuild the existing Baraboo substation in place. The drivers for the rebuild include an older transformer that’s starting to fail and to prepare for a future conversion of the distribution voltage to 24.9kV. Alliant will be providing a portable substation as part of the project. One potential “cost adder” they mentioned was that the city of Baraboo is interested in potentially relocating the substation (see the project notes section for more info). Additional LDC scope if this were to go through includes:Alliant constructing a new substation at the specified site.Alliant to install the distribution equipment at this location instead and retire the existing equipment at the original site. ATC to install new jumpers & insulators to the Alliant transformer. ATC connect/disconnect the portable substation as needed. The ATC scope of work for the substation relocation “cost adder” includes:ATC to replace one existing T-Line structure to re-route the line to the new location.ATC to install two new T-Line structures to re-route the line to the new location.ATC to install necessary conductor (~0.04mi) to re-route to the new location.ATC to install two new dead-end structures inside the substation.ATC to install a new loop through bus (in place of existing box structure).ATC to install new circuit switcher for the shunt capacitor bank at this substation.ATC to install a new 10.4MVAR capacitor bank.ATC to retire 9 existing T-Line structures that would be no longer needed.ATC to retire existing substation equipment at the original substation. | 9/17/25 – Per QP meeting, ISD moves to 12/1/28. 3/6/25- ISD moves to 6/1/28, Site 2 has been selected. 2/28/24- per QP discussion, ISD moves to 06/01/27 10/27/23- ICC email sent to customer. CW letter to follow. 9/27/23- LIRF deemed complete and customer notified | McGowan, Gavin | Alternative Assessment
2024-09-05 | 2024-09-18 | 41033 | Alliant Energy | Blanchardville | Sub Rebuild | 12 | 2030-12-30 | WPL is planning to rebuild the Blanchardville SS ATC scope - Assumed jumpers, insulators and minimal t-line pole replacements. | 3/3/26- CW letter executed and sent to customer2/27/26- CW letter resent for execution 10/16/25 – CW letter sent for signature 3/6/25- ISD moves to 2030 per QP meeting. 10/16/24- initial MCW determination sent to customer, letter to follow 9/18/24- LIRF deemed complete and customer notified | McGowan, Gavin | MCW
2017-09-25 | 2017-10-09 | 40483 | Alliant Energy | Edgewater | New Sub | 24 | 2030-12-31 | Edgewater distribution XFMR relocate to new sub location across the street from generation switch yard. Install one XFMR but have space for two. ATC loop-thru 138 kV line X-37 with two line breakers and make space provision for bus-tie breaker. | 1/23/25-move back to Planning queue until guidance from WPL. Revised LIRF or new LIRF to be submitted? 11/30/22- update from Logan B - ISD moves to 12/31/30. Will cancel the current PR for the project and will be re-issued closer to the ISD. 09/15/20- per QP meeting, ISD moves to 2025 10/9/19- per QP meeting, ISD moves to 12/31/22 03/29/19 PM assigned and customer notified 3/7/19- CW letter executed 10/09/17- LIRF deemed complete and customer notified | McGowan, Gavin | Alternative Assessment
2025-05-30 | 2025-06-12 | 40103-3 | Alliant Energy | Hampden | Sub Rebuild | 18 | 2029-12-31 | WPL to rebuild Hampden Sub with 69/24.9x12.47kV 20 MVA xfmr and 5 circuit distribution bus. ATC to replace jumpers and insulators to the new WPL switch. Sub Rebuild, scope to be updated once LIRF is submitted | 3/27/26 – Per email updates from Nick H, ISD moves to 12/31/29 ​​3/3/26- CW letter executed and sent to customer 2/27/26- resent CW letter to WPL for execution 9/17/25 – Per QP meeting, ISD moves to 12/31/28 7/23/25- CW letter sent to customer for execution 6/12/25- LIRF rev3 deemed complete, customer notified 3/6/25- ISD moves to 06/1/28 8/16/22- ISD moves to 6/1/30 6/15/21- ISD moves to 6/1/28 3/25/20- per QP meeting, ISD moves to 6/1/25 09/11/17- ISD moves to 6/1/23 8/25/08- Added per QP meeting | McGowan, Gavin | MCW
2025-08-12 | 2025-08-25 | 41152-1 | Alliant Energy | Hawk | New Sub | 18 | 2029-12-31 | WPL to construct a new substation with a single 138/24.9 kV, 20/26/33 MVA transformer and 6-feeder switchgear on land owned by Alliant Energy/Wisconsin Power & Light in the UW Research Park. ATC to Tap 13898 at structure 121817 to the new SS and install horizontal mounted in-line switches with Super Whips. | 3/3/26- CW letter executed and sent to customer 2/27/26- resent CW letter for execution 10/21/25- IS followed up on CW letter, no response 10/2/25- CW Letter sent to WPL 8/26/25 – LIRF rev1 deemed complete, customer notified. 7/10/25 - LIRF deemed complete and customer notified. | McGowan, Gavin | Alternative Assessment
2025-11-13 | 2025-12-02 | 41192 | Alliant Energy | Hooterville (Hooterville DER Nautilus) | Distributed Energy Resource | 12 | 2026-12-01 | Third party developer to install a new 5.0 MW solar facility. Alliant to connect the new facility to the distribution side of the Hooterville transformer XF2. ATC to upgrade the following surge arresters to 57 kV MCOV to support the project: Line Y-36 (Dodgeville - Barneveld) both terminals Inform Alliant of potential need for arrester upgrades at Hooterville SS Line Y-209 (Barneveld - Mount Horeb) both terminals Inform Mount Horeb Utilities of potential need for arrester upgrades at Military Ridge SS | 1/12/26- MCW letter sent to customer 12/3/25: DERRF deemed complete, customer notified. | Pirkola, Logan | MCW
2026-01-08 | 2026-01-22 | 41204 | Alliant Energy | Idle Hour | Sub Rebuild | 30 | 2028-07-01 | WPL to rebuild the Idle Hour substation, with a new 20/33 MVA 69-12.47 kV transformer. ATC to consider constructing a radial 69 kV extension, approximately 0.1 miles in length, off the North Monroe – South Monroe 69 kV (Y-87) line. WPL noted in their LIRF that their plans will include provisions for a future 2nd bus when load growth drives expansion at this substation. Review with cross-functional team on if there is a preference to build a loop-through bus now, or wait until WPL is ready to build their 2nd bus. Also check if there are design considerations ATC should make with a 69 kV radial extension to easily accommodate a loop-through configuration in the future. | 3/27/26 – Per email updates from Nick H, ISD moves to 7/1/28 ​​1/22/26- LIRF deemed complete and customer notified | McGowan, Gavin | Alternative Assessment
2026-03-17 | 2026-03-26 | 41252 | Alliant Energy | Lincoln Pumping | Load Addition | 18 | 2029-02-28 | Enbridge to install an additional 3000hp pump, which exceeds the existing XFMRs capacity Load at LPS SS increases from 12 MW to 14.5 MW Enbridge to install an additional XFMR and low side bus to serve the new pump, as well as removing the fence Enbridge to install gang operated disconnect on ATC’s square bus ATC to install jumper and insulators to connect to Enbridge owned disconnect | 3/26/26- LIRF deemed complete and customer notified | McGowan, Gavin | MCW
2025-10-17 | 2025-10-31 | 41180 | Alliant Energy | Manhattan Distribution | New Sub | 30 | 2028-01-01 | Alliant to construct a new 69 kV (or 138 kV) to 12.47 kV substation with 42 MVA transformer, with space provisions for a second transformer and distribution bay. ATC to consider installing 69 kV or 138 kV loop-through straight-bus with line-breakers and bus-tie switch, with provisions for a future bus-tie breaker and second bus-tie switch. Dependent on substation location, ATC to consider extending double-circuit transmission from either the North Beaver Dam – Waupun 69 kV (Y-24) line or the North Beaver Dam – North Randolph 138 kV (X-47) line to the new substation. A specific parcel was not identified as part of this LIRF, but a substation search area is shown in Manhattan Dist Sub Map.pdf. | 2/26/26 – ISD update 1/1/28, WPL to send revised LIRF 1/8/26- per email from Greg Shue, ISD has been shifted out 6 months. Queue updated to reflect 3/1/28 ISD. 12/8/25- ICC email sent to customer, CW letter to follow 10/31/25 - LIRF deemed complete, customer notified | Pirkola, Logan | System Study
2025-11-13 | 2025-12-02 | 41193 | Alliant Energy | Monticello (Monticello DER Nautilus) | Distributed Energy Resource | 12 | 2026-12-01 | Third party developer to install a new 4.0 MW solar facility. Alliant to connect the new facility to the distribution side of the Monticello transformer T41. ATC to upgrade the following surge arresters to 57 kV MCOV to support the project: Line Y-42 (North Monroe - New Glarus) both terminals Inform Alliant of potential need for arrester upgrades at Monticello SS Line Y-208 (Verona - New Glarus) both terminals In Cascade, the Verona Arresters are labeled as on Line Y-42, which does not terminate in Verona Inform Alliant of potential need for arrester upgrades at New Glarus SS | 1/12/26- MCW letter sent to customer 12/3/25: DERRF deemed complete, customer notified | Pirkola, Logan | MCW
2025-09-10 | 2025-09-23 | 41172 | Alliant Energy | Pittsville | Xfmr Repl | 18 | 2027-12-31 | WPL to replace existing transformer with a 20/26/33 MVA transformer. Replace dead-end and circuit switcher with current standard dead-end and a high-side breaker. Energize bus at 24.9 KV. Replace 2000A main breaker and 4 1200A feeder breakers with 27kV rated breakers. ATC to replace single span from structure 152 to new WPL dead-end (DE) structure.ATC to coordinate portable sub connection. | 10/23/25: MCW letter sent9/24/25: LIRF deemed complete, customer notified. | McGowan, Gavin | MCW
2026-03-17 | 2026-03-26 | 41251 | Alliant Energy | Rio Pumping | Load Addition | 18 | 2029-02-28 | Enbridge to install an additional 3000hp pump, which exceeds the existing XFMRs capacity Load at Rio SS increases from 12 MW to 14.5 MW Enbridge to install an additional XFMR and low side bus to serve the new pump, as well as extending the fence WPL to reroute distribution lines underground Enbridge to connect new ground grid into existing Rio ground grid ATC to likely rework jumper to Enbridge owned disconnect Project team and Interconnection Solutions to coordinate if ATC would sell the existing 6104-B switch to Enbridge, or if there would be jumper work associated with Enbridge installing a new switch. | 3/26/26- LIRF deemed complete and customer notified | McGowan, Gavin | MCW
2025-11-03 | 2025-11-20 | 41189 | Alliant Energy | Williams Bay (Williams Bay Nautilus) | Distributed Energy Resource | 12 | 2026-12-01 | Third party developer to install a new 5.0MW solar facility. WPL to connect the new facility to the distribution side of the Williams Bay transformer T01. To support the DER addition, ATC will upgrade transmission system surge arresters as needed on nearby lines. This includes arresters to 106 kV MCOV, Line X-110 (Brick Church - Williams Bay): Both terminals and Line X-44 (Elkhorn - Williams Bay): Both terminals. | 12/22/25: MCW letter sent 11/20/25: DERRF deemed complete, customer notified | Pirkola, Logan | MCW
45952 | 45979 | 41187 | Cedarburg Light ＆ Water | Cedarburg Central | New Sub | 48 | 2035-12-31 | Cedarburg Light and Water to construct a new substation on the North or East side of Cedarburg, with a single 30/60 MVA 138 kV to 25 kV transformer, and transfer a portion of the existing Cedarburg load to this new substation. ATC to consider tapping into one of the circuits on the double circuit Saukville – Mequon 138 kV (8263) / Saukville – Cedarburg South (8253) Lines and extend 138 kV to the new Cedarburg Substation. Cedarburg’s preferred site would entail an approximate 1.4 mile extension. Cedarburg’s less preferred site would be adjacent to the above 8263/8253 double-circuit line. Planning preference would be to tap into Line 8263 to place the new Cedarburg Central SS on a different line than the existing Cedarburg South SS, or to add a line breaker on the Cedarburg South terminal of Line 8253. An alternative would be to loop the tapped line into the new Cedarburg Central SS, and construct a loop-through bus for the new substation. This isn’t called for with the proposed Cedarburg Central SS ultimately having only 1 transformer. | 2/11/26- revised ICC email sent to customer. Requesting meeting to discuss proposed alternatives 12/17/25- ICC email sent to customer 11/18/25- LIRF deemed complete and customer notified | McGowan, Gavin | Alternative Assessment
2026-01-09 | 2026-01-23 | 41208 | City of Escanaba | Northshore (Whitetail Solar Farm) | Distributed Energy Resource | 18 | 2026-11-01 | Escanaba to install a new 1.4MW solar facility (known as Whitetail Solar Farm). Escanaba to connect DER to Northshore Substation NS1 distribution transformer To support the DER addition, ATC will upgrade transmission system surge arresters as needed on the nearby lines. This includes arresters to 57kV MCOV on line ESCANABA1: Delta terminal. | 2/20/26 – MCW letter sent to customer 1/23/26 – DERRF deemed complete, customer notified | McGowan, Gavin | MCW
2025-03-10 | 2025-03-21 | 41112 | Cloverland Electric Cooperative | Kincheloe 10 MW | Load Addition |  | 2025-08-01 | Kincheloe 23 SS, DIC, 10 MW load addition - Tap existing distribution network to serve load addition. ATC Scope - The scope of work identified in the CEC Kincheloe 10 MW LIRF only involves distribution work, however it needs to be confirmed whether ATC system upgrades are needed to support this load addition. Capital Work Status to be determined, lead time to be determined. | 4/25/25- ICC email sent to customer. ATC to complete SIS. 3/21/25- LIRF deemed complete and customer notified | Pirkola, Logan | System Study
2025-03-10 | 2025-04-02 | 41113 | Cloverland Electric Cooperative | Kincheloe 4 MW | Load Addition |  | 2025-08-01 | Kincheloe 23B SS, DIC, 4 MW load addition. CEC to tap existing distribution network to serve load addition. ATC Scope of Work: Kincheloe 23B was originally planned to be retired as part of the construction of the new Kincheloe 23 substation. If Kincheloe 23B is to remain in service, there likely will need to be transmission line changes made to accommodate this. In addition to the item above, it needs to be determined if ATC system upgrades are needed to support this load addition along with the additional 10 MW proposed at the new Kincheloe 23 substation. Capital Work is assumed | 6/16/25- CW letter executed 4/25/25- ICC email sent to customer. ATC to complete SIS. 4/2/25- LIRF deemed complete and customer notified | Pirkola, Logan | System Study
2025-01-16 | 2025-01-29 | 41082 | Cloverland Electric Cooperative | Magazine (USACE DER) | Distributed Energy Resource | 12 | 2026-02-02 | A third-party developer will install 6.0 MWs of natural gas DER. CEC to perform the connection of the new DER to the distribution side of the Magazine transformer T1. ATC Scope - NCW (Note DER AFS is required) | 5/5/25- held DER AFS discussion with CEC and DER developer. 2/27/25- NCW letter sent to customer. Will remain on planning queue until DER AFS study is complete. 1/29/25- DERRF deemed complete and customer notified | Pirkola, Logan | NCW - LDC Only
2021-11-19 | 2021-12-03 | 40744 | Columbus Water ＆ Light | Columbus | Xfmr Repl | 24 | 2028-06-01 | Columbus requests collaboration to determine the Best Value Plan for a variety of alternatives for replacing and/or adding a transformer in the Columbus area. ATC scope of work: Initiate BVP evaluation. Largest scope would construct a 69 kV loop through bus with switches at Maple Avenue and a 69 kV loop through bus with line breakers at Columbus South. Build 1 mile of new 69 kV line and acquire 1.4 miles of 69 kV line from Columbus. | 3/25/25 - ISD updated via Forster meeting 2/7/25- Status update sent to Forster regarding BVP drafting and next steps. 12/20/24- Submitted in Exto in Dec 2024, PI144 ​8/3/23- per internal discussions, ISD is pushed out to 6/1/26. Project is currently in a holding pattern. 12/22/21- ICC/capital work determination sent to customer 12/3/21- LIRF deemed complete and customer notified | McGowan, Gavin | Alternative Assessment
2023-02-07 | 2023-02-21 | 40847 | Cuba City Water & Light | Cuba City - Jefferson Street | Retirement | 54 | 2031-10-15 | Cuba City to retire their Jefferson St substation with the completion of the loop-through 69 kV straight bus at their Monroe St substation. ATC will consider completing the loop-through 69 kV straight bus associated with the installation of Cuba City’s 2nd transformer. Provisions for future 69 kV line and bus-tie breakers. ATC will consider line breakers if needed. With the completion of the Monroe St loop-through bus and the retirement of Jefferson St, ATC will consider T-line routing options to loop Y-130 in and out of the Monroe St substation | 12/5/23- CW letter executed with all three phase, including retirement. ​​3/21/23- ICC email with CW determination sent to customer ​02/21/23- LIRF deemed complete and customer notified | McGowan, Gavin | Alternative Assessment
2025-10-30 | 2025-11-13 | 41185 | Gladstone Power ＆ Light | North Bluff | Xfmr Repl | 12 | 2027-09-01 | Gladstone to replace existing transformers T1 and T2 with 2 new 69 kV to 13.09 kV 7.5/10.5 MVA transformers, retire control house “Building #1”, and modify their AC service to have primary & backup capabilities in the main shared ATC/City control building, “Building #2”.ATC to establish a project team and perform a site visit to determine the final removal or relocation of existing equipment in control house Building #1 to control house Building #2. | 12/12/25: MCW letter sent11/13/25- LIRF deemed complete and customer notified. | Pirkola, Logan | MCW
2025-08-11 | 2025-08-22 | 41133-1 | Jefferson Utilities | Crawfish River (Kikkoman) | Load Addition | 30 | 2026-01-01 | For the Kikkoman load addition (LIRF #41133-1), Jefferson Utilities will reroute two existing trunk feeders from Crawfish River to Kikkoman’s new development. The load will be served from the Crawfish River distribution transformer T8, but will ultimately be served from transformer T7 under normal distribution system conditions. For the Onego Bio load addition (LIRF #41134-1), Jefferson Utilities will construct two new distribution trunk feeders (one from each transformer) stemming from the Crawfish River substation. Onego Bio will initially be served from one existing trunk feeder fed from each of the two transformers. The new trunk feeder fed from transformer T8 will be used to serve half of the development under normal distribution system conditions while the new trunk feeder fed from transformer T7 will act as a backup under contingency. ATC to install one line breaker and one bus side disconnect switch on line 6654 (Crawfish River – Jefferson). ATC to replace circuit switcher 9043 with one line breaker on line 9043 (Crawfish River – Concord).ATC to replace the existing RTU panel in the Crawfish River control house with a new standard RTU panel. | 10/27/25- CW letter executed 8/22/25- LIRF rev1 deemed complete and customer notified 6/9/25 - initial capital work determination email sent. 5/9/25- LIRF deemed complete and customer notified | McGowan, Gavin | Alternative Assessment
2025-08-11 | 2025-08-22 | 41134-1 | Jefferson Utilities | Crawfish River (Onego Bio) | Load Addition |  | 2027-12-31 | For the Kikkoman load addition (LIRF #41133-1), Jefferson Utilities will reroute two existing trunk feeders from Crawfish River to Kikkoman’s new development. The load will be served from the Crawfish River distribution transformer T8, but will ultimately be served from transformer T7 under normal distribution system conditions. For the Onego Bio load addition (LIRF #41134-1), Jefferson Utilities will construct two new distribution trunk feeders (one from each transformer) stemming from the Crawfish River substation. Onego Bio will initially be served from one existing trunk feeder fed from each of the two transformers. The new trunk feeder fed from transformer T8 will be used to serve half of the development under normal distribution system conditions while the new trunk feeder fed from transformer T7 will act as a backup under contingency. ATC to install one line breaker and one bus side disconnect switch on line 6654 (Crawfish River – Jefferson). ATC to replace circuit switcher 9043 with one line breaker on line 9043 (Crawfish River – Concord).ATC to replace the existing RTU panel in the Crawfish River control house with a new standard RTU panel. | 10/27/25- CW letter executed 8/22/25- LIRF rev1 deemed complete and customer notified 6/9/25 - initial capital work determination email sent 5/12/25- LIRF deemed complete and customer notified | McGowan, Gavin | Alternative Assessment
2025-07-03 | 2025-07-21 | 41154 | Madison Gas ＆ Electric | American | Additional Xfmr |  | 2028-04-30 | MGE to install a new 138kV/13.8kV distribution transformer and 13.8kV switchgear at American Substation.ATC to install 2 138kV line breakers, one 138kV bus-tie breaker and new ATC only control building at American. | 2/25/26- per update from planning leadership, kick off for project team is targeted for May 2026. Breaker is already in material forecast so no impact to overall schedule. 9/3/25- CW letter executed 7/21/25- LIRF deemed complete and customer notified 6/24/25 - per monthly check-in meeting, adding to potential queue to keep track of project status. | McGowan, Gavin | Alternative Assessment
2024-12-20 | 2025-01-28 | 41070 | Marquette Board of Power ＆ Light | New Sub #8 | New Sub | 30 | 2026-12-31 | Marquette Board of Light and Power (MBLP) is proposing a new T-D substation with one 138-12.47 kV 20/37.3 MVA transformer on the west side of Marquette. ATC will consider installing a radial feed to new substation Consider the alternative of a 138 kV loop through straight bus with switches. | 5/12/25- update sent to MBLP noting the need for a full SIS. 2/27/25- initial capital work email sent to customer 1/28/25- LIRF deemed complete and customer notified | Pirkola, Logan | System Study
2026-01-09 | 2026-01-23 | 41205 | Menasha Utilities | Northside | High Side Protection Replacement | 18 | 2027-10-01 | Menasha Utilities to replace the 138CS24 circuit switcher on the high side of XFMR T24. ATC to modify bus side 3.5” IPS bus conductor due to the new circuit switcher having shorter dimensions. | 3/9/26- MCW letter sent to customer 1/23/26- LIRF deemed complete and customer notified. | McGowan, Gavin | MCW
2026-01-09 | 2026-01-23 | 41206 | Menasha Utilities | Tayco | High Side Protection Replacement | 18 | 2027-10-01 | Menasha Utilities to replace the 138CS24 circuit switcher on the high side of XFMR T24. ATC to modify bus side 3.5” IPS bus conductor due to the new circuit switcher having shorter dimensions. | 2/27/26- MCW letter sent 1/23/26 – LIRF deemed complete, customer notified | McGowan, Gavin | MCW
2025-10-30 | 2025-12-04 | 41195 | Oconto Electric Cooperative | OEC New Distribution SS | New Sub | 30 | 2029-06-01 | OEC to construct a new 138 kV to 34.5 kV substation with a 50 MVA transformer, with space provisions for a second transformer. ATC to consider installing a 138 kV loop-through straight-bus with bus-side line-switches and bus-tie switch, with provisions for future line-breakers, line-side line-switches, bus-tie breaker, and second bus-tie switch. ATC will consider extending a double-circuit 138 kV line. The specific line to be extended cannot be determined until OEC procures a parcel for their new substation and cross-functional review input is received. A specific parcel was not identified as part of this LIRF, but the LIRF indicates that OEC would prefer to have the new substation within 1 mile of an existing ATC 138 kV transmission line and near the ATC Morgan Substation. | 1/13/26- ICC email sent to customer. CW letter to follow once OEC selects parcel for new substation. 12/4/25- LIRF deemed complete and customer notified | Pirkola, Logan | Alternative Assessment
2025-09-26 | 2025-09-30 | 41168-1 | Rock Electric Cooperative | Innovation Park Substation | New Sub | 30 | 2028-03-31 | REC will construct a new Innovation Park substation with one new 138/12.47 kV, 30/40/50 MVA transformer with high-side circuit breaker. ATC will loop in and out the Janesville General to Rock River (X-24) line (Venture to Rock River line section). ATC will construct a 138 kV loop through bus at the new substation and install two 138 kV line switches and two 138 kV bus side switches and two 138 kV line breakers ATC will allow space provisions for two future 138 kV bus-tie disconnect switches and future 138 kV bus-tie breaker. | 10/21/25 – signed CW letter received 9/30/25- LIRF rev1 deemed complete and customer notified. 9/2/25- LIRF deemed complete and customer notified | McGowan, Gavin | Alternative Assessment
2026-03-02 | 2026-03-24 | 41249 | Slinger Utilities | Arthur Road | Additional Xfmr | 30 | 2028-06-01 | Slinger Utilities to install an additional transformer (26.2/138 kV, 30/56 MVA) at the jointly owned Arthur Road Substation. The substation is owned by Hartford and Slinger. Slinger Utilities to install one 138 kV circuit switcher, and one 25 kV main circuit breaker. ATC to install bus-tie breaker and second bus-tie switch Arthur Road crosses 30 MW in 2028, requiring the bus-tie breaker ATC to evaluate installing the switch and bus-tie separately, given the long lead time for the breaker Installing the switch with this XFMR addition would decrease the difficulty in the bus-tie breaker installation ATC to incorporate the new XFMR into the protection scheme and EMS LDC owned switch (T42-A) is already installed, so likely no jumper work associated with connecting the XFMR. | 3/24/26- LIRF deemed complete, customer notified3/25/25- added to potential queue per Forster meeting. | McGowan, Gavin | Alternative Assessment
2026-03-02 | 2026-03-24 | 41248 | Sturgeon Bay Utilities | First Ave | Xfmr Repl | 18 | 2028-08-01 | Sturgeon Bay Utilities (SBU) to replace existing T1 XFMR (12.47/69 kV, 20/22.4 MVA) with slightly larger transformer (13.09/67 kV, 15/28 MVA) to match other SBU owned transformers. SBU to replace the two 69kV circuit breakers on T1 and T2, and the high side 69 kV switch for T1. SBU to install or renew oil containment for both transformers. SBU to upgrade auxiliary controls relating to 12 kV automatic transfer scheme. ATC to install jumpers and insulators to accommodate new high side 69kV switch for T1. Insulator need to be confirmed during cross-functional review. | 3/24/26- LIRF deemed complete and customer notified 3/25/25- potential project added at Forster check in meeting | McGowan, Gavin | MCW
2026-03-02 | 2026-03-20 | 41239 | Waunakee Utilities | Division Street | Xfmr Repl |  | 2026-06-01 | Waunakee Utilities to replace existing 14 MVA transformer with new 12.47/69 kV XFMR with a rating of 15/28 MVA. Waunakee Utilities to install associated control and relay equipment, as well as a new set of Voltage regulators The scope of work identified in the LIRF does not include any capital work for ATC. The existing high-side switch, the demarcation point, is not changing and thus there is likely no scope associated with this project. Confirm during cross-functional review | 3/20/26- LIRF deemed complete, customer notified | McGowan, Gavin | NCW - LDC Only
2021-08-19 | 2021-09-01 | 40711 | We Energies | Caledonia | New Sub | 36 | 2030-12-01 | WEC to construct a new Caledonia Substation with two 138/24.9 kV transformers. ATC scope of work: ATC to extend 138 kV transmission line (4-6 mi) to loop-through the new Caledonia Substation. | 09/05/25- LIRF rev1 deemed incomplete due to load forecast inconsistencies 3/11/25- LIRF rev1 received 12/4/24- per QP discussion, ISD moves to 12/1/30. 9/13/23- ISD moves to 6/1/30 ​​4/10/23- ISD moves to 6/1/2028 per QP meeting 9/15/22-ISD moved to 6/1/27 9/29/21- ICC email sent to customer, LIRF to reb routed at a later date 9/1/21- LIRF deemed complete and customer notified 3/4/21- added per QP meeting | Pirkola, Logan | Alternative Assessment
2025-10-02 | 2025-10-16 | 41099-1 | We Energies | Goodhue | New Sub | 48 | 2028-12-25 | WEC to build a new substation in Johnson Creek, with 2 transformers and 2 busses to shift load from Concord. ATC to consider installing a 138 kV loop through straight bus with line breakers and bus-tie switches, with provisions for a future bus-tie breaker ATC to extend double-circuit 138 kV from the Crawfish River – Concord 138 kV (9043) line to the new substation. WEC is still seeking a property for this substation | 12/4/25 – per QP meeting, ISD moves to 12/25/28 11/20/25- ICC email for rev1 sent to customer 10/16/25 – LIRF rev1 deemed complete, customer notified. 9/5/25- LIRF rev request sent to customer, requested due to load forecast inconsistencies 5/29/25 - per QP meeting, project name change to Goodhue. 4/4/25- ICC email sent to customer. Follow up with ICC email at later date. 3/7/25- LIRF deemed complete and customer notified 3/13/24- ISD updated to 6/1/28 at QP meeting 2/14/22- per QP meeting, ISD moves to 6/1/26 3/4/21- per QP meeting, the ISD moves to 2025. 2/25/19- per QP meeting, ISD moves to 6/1/24 2/26/18- per QP meeting, ISD moves from 2020 to 2022 08/22/14- per QP meeting, ISD moves from 2019 to 2020 02/25/14 per QP meeting, ISD moves from 2018 to 2019 11/01/13 Customer to submit a LIRF for review | Pirkola, Logan | Alternative Assessment
2025-07-09 | 2025-09-03 | 41170 | We Energies | Milwaukee County Z | Additional Xfmr | 9 | 2026-12-31 | WEC to add 138-24.9 kV T8 and Bus 8 at Milwaukee County SS, with associated foundations for transformer, and PDC. ATC to update the protection schemes and if required, will install equipment needed to accommodate the protection changes. | 12/4/25 – per QP meeting, ISD moves to 12/31/26 10/21/25 – MCW letter sent 9/4/25 - LIRF deemed complete 9/3 - customer notified on 9/4. 5/29/25 - ISD moved to 12/1/26 per QP meeting. ​​4/10/23- ISD moves to 6/1/2026 per QP meeting 3/3/21- ISD moves to 6/11/25, was 2024 2/25/19- added per QP meeting. | Pirkola, Logan | MCW
2024-11-22 | 2024-12-11 | 41062 | We Energies | North Saukville DIC (Woodview Lane/Charter Steel) | New Sub | 30 | 2027-03-31 | LDC requesting ATC to perform a sectionalizing review LDC customer requesting ATC to relocate transmission line to the north of existing line ATC to consider building a double-circuit extension with line breakers and bus-tie breaker ATC to consider relocating line to the north of existing line per request | 2/17/26- executed BVP report returned to WEC 2/9/26- BVP report sent to WEC for execution, executed by WEC same day. 9/25/25 – per QP meeting, ISD moves to 3/31/27 09/05/25- per PCA Committee, PCA not required for this project. 3/5/25- internal cross functional meeting held. 1/14/25- ICC email sent to customer. BVP report or CW letter to be determined. 12/11/24- LIRF deemed complete and customer notified | Pirkola, Logan | Alternative Assessment
2025-07-23 | 2025-08-05 | 41162 | Wisconsin Public Service | Goodman | Other | 0 | 2030-12-01 | Goodman SS, DIC, Transmission Reliability Review - no ISD identified No LDC work identified in LIRF ATC to perform a reliability review of the transmission service at Goodman SS, following the ATC Additional Source Review procedure. | 9/5/25- ICC email sent to customer 8/5/25- LIRF deemed complete, customer notified | Pirkola, Logan | TBD
2025-07-23 | 2025-08-06 | 41164 | Wisconsin Public Service | Mountain | Other | 0 | 2030-12-31 | No LDC work identified in LIRF Requested ISD: N/A ATC Scope of Work: ATC to perform a reliability review of the transmission service at Mountain SS, following the ATC Additional Source Review procedure. | 9/5/25- ICC email sent to customer 8/6/25- LIRF deemed complete and customer notified | Pirkola, Logan | TBD
2025-03-17 | 2025-03-31 | 41115 | Wisconsin Public Service | Oconto | High Side Protection Replacement | 18 | 2028-06-01 | WPS to replace Bank 1 and Bank 2 circuit switchers, upgrade protective relays, voltage regulators, and feeder exit reclosers. WPS requesting ATC to review if a bus-tie breaker would be warranted at the substation. Will be reviewed with ATC functional areas. | 3/4/26- ISD moves to 6/1/28 10/2/25 - WPS to pursue full rebuild, updated LIRF to be submitted. ISD moved to 12/1/28 4/25/25- ICC email sent to WPS, CW or MCW letter to follow, TBD. 3/31/25- LIRF deemed complete and customer notified | Pirkola, Logan | MCW
2026-01-27 | 2026-02-10 | 41215 | Wisconsin Public Service | Sherwood | High Side Protection Replacement | 12 | 2027-02-01 | Replace 199 and 299 circuit switchers, Feeder 241 and 242 reclosers, and Feeder 241 and 241 relays. A mobile substation will be needed to support this project. ATC will need to support the connection and disconnection of the WPS mobile substation for this project. ATC may need to perform jumper replacement work to support the circuit switcher replacement. | 3/26/26- MCW letter sent to customer 2/10/26- LIRF deemed complete, customer notified | Pirkola, Logan | MCW
2025-07-23 | 2025-08-05 | 41163 | Wisconsin Public Service | Silver Cliff | Xfmr Repl | 18 | 2028-04-01 | WPS to replace Bank 1 transformer with 22.4 MVA transformer, replace high-side fuses with circuit breaker, replace transmission structure and 199 SW, install new breakers on Feeder 241, and replace control house. ATC to disconnect and reconnect to the WPS dead-end structure, and may require ATC to replace the tangent pole just outside of the Silver Cliff Substation. ATC to also perform the connection and disconnection of the portable substation needed to support this project. | 3/4/26- ISD moves to 4/1/28 9/19/25 - MCW letter sent 8/6/25 - LIRF deemed complete, customer notified. 6/10/25 - per QP meeting, looking to pull into 2026 based on xfmr availability. Wasn't sure of the ISD just yet. ​8/22/23- per email from Dan Parent, ISD moves out to 12/1/27 2/26/20- Added to potential queue per QP meeting | Pirkola, Logan | MCW
2025-07-23 | 2025-08-06 | 41165 | Wisconsin Public Service | Silver Cliff | Other |  | 2030-12-31 | No LDC work identified in LIRF ATC to perform a reliability review of the transmission service at Silver Cliff SS, following the ATC Additional Source Review procedure. | 9/5/25- ICC email sent to customer 8/6/25 - LIRF deemed complete, customer notified. | Pirkola, Logan | TBD
2024-09-23 | 2024-10-10 | 41045 | Wisconsin Public Service | University | Xfmr Repl | 18 | 2028-12-31 | WPS to replace Bank 1 and 2 transformers with two (2) new base 7 MVA 69/12.47 kV transformers, replace fused high side with circuit switchers, and other distribution equipment replacements. Further outreach to WPS indicates possible replacement of high-side 69kV switches. Mobile substation required to support work. ATC Scope of Work: The scope of work identified in the University LIRF may require jumper replacement work for the high-side 69kV switches. Provide jumpered connection to mobile substation Minimal Capital Work is assumed due to the likelihood of WPS replacing their 199 and 299 switches at University SS | 10/2/25 - ISD updated to 12/31/28 12/2/24- per QP meeting, ISD is 9/1/26, before start of UWGB school year. 11/7/24- MCW letter sent to customer 10/10/24- LIRF deemed complete and customer notified 6/9/22- ISD moves to 12/1/26 per QP meeting 2/26/20- added to potential queue per QP meeting | Pirkola, Logan | MCW

## Project Management
2026-04-08
ISD has passed
ISD is within 90 days of Queue posting
LIRF/DERRF Received | LIRF/DERRF Complete | LIRF/DERRF ID # | Distribution Customer | Project Name | Project Type | Estimated ATC Project Lead-Time After PCA Execution | Requested In-Service Date | Projected Scope of Work | Notes & Updates | ATC Project Manager | BVP Type
2022-04-27 | 2022-05-11 | 40773 | Adams Columbia Electric Cooperative | Colburn | New Sub | 36 | 2025-09-01 | ​ACEC will construct a new 69 kV substation with one 69/12.47 kV 10/14 MVA transformer with fuses for H-S protection. ATC will consider networking with a new 69 kV line from ACEC Cottonville to either Hancock or ACEC Coloma to interconnect the new ACEC Colburn Substation. Either a new switching station would be needed at the ACEC Coloma tap or Hancock would be expanded. | 1/31/25- CA filed with PSCW ​8/1/23- PM assigned and customer notified ​7/12/23-BVP report fully executed, PR submitted ​06/09/22- ICC email sent to customer, with note it will be a capital work project 05/11/22- LIRF deemed complete and customer notified | Lyons, Jason;#153 | Alternative Assessment
2019-05-22 | 2019-06-17 | 40571 | Alliant Energy | Badger Pumping Station | Retirement | 18 | 2026-12-31 | Pending customer agreement, Badger Pumping substation will be retired. Load will be served from distribution service. ATC to retire 4 mile Y-38 tap from BPS to BPST, may also retire another 3.5 mile Y-38 from JAN to PHT and line terminal at JAN. | 11/8/24- PM reassigned email sent to customer 6/12/24- per QP meeting, ISD moves to 12/31/26 8/16/22- ISD moves to 12/31/24 9/16/21- per update from Bob G, ISD to be moved to 12/31/22. 3/9/21- Per QP meeting, ISD moves to 12/31/21 9/28/20- per email from Bob G, ISD moves to 6/1/21. 4/8/20- PM assigned and customer notified 4/3/20- CW Letter executed and email back to customer 6/17/19- LIRF deemed complete and customer notified | Nett, Jason;#1101 | Alternative Assessment
2021-10-22 | 2021-11-03 | 40729 | Alliant Energy | Belleville | Sub Rebuild | 18 | 2027-03-01 | WPL will replace the existing transformer at the Belleville Substation due to age and condition and add a second transformer for reliability issues. Both transformers will be 69/24.9/12 kV 12/16/20 MVA transformers with a 2000 amp circuit breakers on the high-side. ATC will rebuild the Belleville Substation with a loop through substation insulated to 138 kV with manual line and bus-tie switches with provisions for future line and bus-tie breakers. | 12/9/25: Per QP Meeting, ISD moves to 3/1/27 ​8/1/23- transitioned to project management. PM to be reassigned and IS to send email to Alliant with updated contact. ​2/14/23- executed CW letter sent to customer 8/16/22- ISD moves to 12/31/26 12/1/21- ICC email sent to customer 11/03/21- LIRF deemed complete and customer notified 6/12/19- Added to potential list during quarterly planning meeting. | Lyons, Jason;#153 | Alternative Assessment
2025-01-13 | 2025-01-15 | 41079 | Alliant Energy | Cambridge | High Side Protection Replacement | 12 | 2026-12-31 | Due to expected fault current increases in the area, WPL to replace the 138 kV circuit switcher with a 138 kV GOAB switch and 138 kV 2000A breaker. The 138kV GOAB will be installed on the existing Dead End along with inverted line arresters. The 138kV Breaker will be placed where the old 138kV Circuit Switcher was physically located. There will be no changes to the power transformer or distribution equipment. ATC to install new jumpers and insulators to the new WPL 138kV GOAB switch. ATC to perform the connection/disconnection to the WPL portable substation (if required). | 12/9/25: Per QP Meeting, ISD moves to 12/31/27 ​5/9/25 - PM assignment email sent, Bobby L. 2/12/25- MCW letter sent to customer 1/15/25- LIRF deemed complete and customer notified | Lampshire, Robert;#112 | MCW
2016-06-10 | 2016-06-23 | 40415 | Alliant Energy | Camp Douglas | Xfmr Repl | 24 | 2025-12-31 | Transformer Replacement | 9/26/23- ISD moves to 12/31/25 per QP discussion ​8/2/23- PM assigned email sent to customer ​6/15/23- CW letter executed ​2/2/23- Alliant shared preliminary layout with ATC via email 12/29/22- CW assessment email sent to customer, CW letter to follow. 1/31/20 - per QP meeting, ISD moves to 6/1/25 6/15/21- per QP meeting, ISD moves to 6/1/24, move back to planning queue. Alliant to resubmit LIRF if scope change 08/07/18- per QP meeting, ISD moves to 6/1/28 1/22/18- per LIRF list from Chris Allen, ISD is 2023. ISD moved to 6/1/23 and will be reviewed at first 2018 D-T check in meeting. 08/09/16- per QP meeting, project will be moved to inactive on-hold due to ISD, Planning to review project for active status on 3/1/21 06/23/16- LIRF deemed complete and customer notified | Berton, Doug;#115 | MCW
2023-04-13 | 2023-04-27 | 40858 | Alliant Energy | Cottage Grove | High Side Protection Replacement | 18 | 2026-08-01 | Alliant will retire the existing Cottage Grove substation equipment, and relocate the new substation fence to the southeast. Alliant will install a 69 kV circuit breaker, a new 69/12.47 kV, 15/20/25 MVA transformer and install a new control house with new batteries and relaying. ATC will retire the existing Cottage Grove Tap 3-way switching structure (COGT, STR 313) and replace with a new structure.ATC will retire the existing STR 139 wood pole structure, and replace with a new 3-way switching structure. | 3/6/25- ISD moves to 8/1/26 per QP meeting. 12/9/24- ISD moves to end of December 2025 2/28/24- per QP discussion, ISD moves to 06/01/25 10/26/23- PM assigned email sent to customer ​8/31/23- updated ISD per Alliant from 2026 to 2024 6/12/23- CW letter executed ​5/25/23- ICC email with CW letter sent to customer. ​4/27/23- LIRF deemed complete and customer notified 4/5/23- added to potential queue | Berton, Doug;#115 | Alternative Assessment
2023-07-21 | 2023-08-04 | 40171-1 | Alliant Energy | Dana | Sub Rebuild | 18 | 2028-12-31 | Alliant to rebuild the existing Dana Corp (DAC) substation. This includes: Alliant to replace existing substation transformer and replace existing low side switchgear. Alliant to replace existing high side fuses with circuit switchers and will do some minor physical rearrangement of the equipment at substation site. ATC to review and adjust line protection settings if needed. Assuming it won’t be needed as the circuit switchers are an improvement from the fuses, but system protection to make final determination. ATC to relocate (or provide new) the existing dead-end structure to support the substation rearrangement. | 6/3/25 - per QP meeting, working through real estate issues. ISD moves to 12/31/28. 5/29/24- PM assigned and customer notified, will be managed by ECI with oversight from Bobby L 4/22/24- CW letter executed 9/26/23- ISD moves to 12/31/26 per QP discussion ​8/31/23- ICC email sent to WPL with CW determination, letter to follow ​08/04/23- LIRF deemed complete and customer notified 9/15/21- ISD moves from 2023 to 2024 6/12/19- ISD moves to 2023 09/11/17- ISD moves to 12/30/22 4/4/17- per Alliant, move Dana off of project management queue and place in potential, new LIRF to be submitted 02/23/16- per email from Alliant, ISD moves from 6/1/121 to 12/31/20 01/30/15- per Alliant schedule, ISD moves from 2020 to 2021 2/12/14- per Alliant, ISD moves from 6/1/17 to 2020 12/09/13 Alliant submitted a new LIRF (Pioneer) that will swap ISDs with this project; the revised ISD will change from 06/01/15 to 06/01/17 11/12/11 e-mail changing ISD from 13 to 15 | Lampshire, Robert;#112 | Alternative Assessment
2025-02-06 | 2025-02-24 | 41032-1 | Alliant Energy | East Beloit | Sub Rebuild | 24 | 2027-12-30 | WPL will construct a new substation with two new 138/12.47kV, 12/20 MVA transformer with a high-side circuit breaker. ATC will loop through the new substation from the Colley Road – Beloit Gateway (X-41) line between Colley Road and Dickinson line section. ATC will construct a 138 kV loop through bus at the new substation and install two 138 kV line switches and two 138 kV bus side switches and allow space provisions for future 138 kV line breakers. ATC will install two 138 kV bus-tie disconnect switches and allow space provisions for a future 138 kV bus-tie breaker at the new substation. ATC to retire the existing Colley Road – East Beloit (Y-140) line. ATC to install two 138 kV line circuit breakers and two 138 kV line disconnects at Dickinson substation and remove load break bottles from the existing 138 kV load break switches - 6345LB and 6346LB. | 3/13/25- PM assigned email sent to customer 3/11/25- CW letter executed 2/24/25- LIRF revised due to location update and ISD update. No major change to ATC Scope. 10/16/24- ICC email sent to customer. CW letter to follow 9/18/24- LIRF deemed complete and customer notified | Gerdes, Michelle;#930 | Alternative Assessment
2022-10-11 | 2022-10-25 | 40814 | Alliant Energy | East Pittsville | New Sub | 54 | 2028-12-31 | ​WPL will construct a new138kV substation with one 138/24.9-12.4 kV 33 MVA transformer. ATC Scope of Work: ATC to construct a green field 138 kV switching station on X-42 and to build a greenfield 138 kV line to new Gardner Substation. | 6/3/25 - per QP meeting, name change from Gardner to East Pittsville. 12/11/24- PCA Committee met and reviewed PCA need. ATC will not proceed with a PCA for this project. 11/21/24- PM assigned and customer notified - Note BVP report in progress and to be completed. 1/22/22- ICC email sent to customer 10/25/22- LIRF deemed complete and customer notified 8/16/22- added to potential queue per D-T Check In meeting | LeMere, Tim;#827 | Alternative Assessment
2024-04-18 | 2024-05-01 | 40973 | Alliant Energy | Fountain Valley | Xfmr Repl | 12 | 2027-12-31 | WPL to replace the existing transformer (T41) at Fountain Valley with a new 69/12.49kV 10/12.5 MVA unit. WPL to replace their high side protective devices with a new2000A circuit breaker (5003-S) and a visible disconnect switch (5003-L). WPLwill also modernize their system protection and install SCADA for monitoring and control. ATC will provide new jumpers/insulators to support the installationof the new high side disconnect switch (5003-L). ATC will also provide support for the portable sub needed for this project. | 5/12/25 - sent PM assigned email, Bobby Lampshire 12/20/24- project intake submitted in Exto - PI143 5/29/24- MCW letter sent to customer 5/1/24- LIRF deemed complete and customer notified | Lampshire, Robert;#112 | MCW
2023-09-13 | 2023-09-27 | 40894 | Alliant Energy | Houghton Rock | Xfmr Repl | 24 | 2027-08-01 | WPL to do a complete rebuild of the Houghton Rock substation in place, including a 69/12.47 kV, 20 MVA transformer and five overhead feeders connected to the 12.47 kV bus. ATC will provide a temporary portable substation connection. ATC will install new jumpers and insulators in the newly rebuilt Houghton Rock substation. | 6/3/25 - per QP meeting, ISD moves to 8/1/27. 9/19/24- ISD update to 2027 per WPL/Greg A via email 4/9/24- PM assigned email sent to customer 2/28/24- per QP discussion, ISD moves to 12/31/26 12/4/23- per update from Ryan/Alliant, ISD moves to 12/31/25. 10/26/23- MCW letter and ICC sent to customer 9/27/23- LIRF deemed complete and customer notified ​8/16/22- added to potential queue per D-T Check In Meeting | Gerdes, Michelle;#930 | MCW
2023-10-25 | 2023-11-10 | 40922 | Alliant Energy | Kieler | Sub Rebuild | 36 | 2026-05-01 | WPL Kieler rebuild project. Retiring the existing single transformer Kieler substation, and constructing a new 2-transformer ultimate substation along the planned ATC route. WPL plans to purchase and construct a new 69 kV substation with two 69/12.47 kV, 12/20 MVA transformers. WPL will make provisions for future 25 kV distribution service. ATC Scope of Work: If located a relatively larger distance away (>0.2 miles) from AY substation. New loop-through substation with manual disconnect switches (assume load-breaking attachments). ATC will provide additional loop-through transmission service along the planned Grant County DIC scope route. Retire Kieler sub termination. | 10/3/25- per update from Nick H, ISD moves to 5/1/26. 12/20/24- BVP report executed. Already with project management for precert activities. This has moved to PM. 9/19/24- revised ISD provided by Greg A via email 12/18/23- ICC sent to WPL. Will be a part of the BVP report with the other Kieler projects. 11/10/23- LIRF deemed complete and customer notified |  | Alternative Assessment
2023-03-31 | 2023-04-04 | 40855 | Alliant Energy | Lake Geneva (Downtown) | Xfmr Repl | 24 | 2027-06-01 | ​Two alternatives include expanding the current location or relocating more north to a new substation location. Worst-case assumption – new substation.Alliant will build a new substation with one 69/12.4-24.9 kV, 20/33 MVA transformer, with ultimate plans for two transformers. ATC Scope of Work: ATC will consider installing two dead-end structures to terminate into the new Alliant substation. ATC will consider building a loop-through 69 kV bus with switches. ATC will consider retiring the 3-way GOAB devices on the LAGT tap structure, and reuse the existing structure (Jumper through) | 6/3/25 - per QP meeting, ISD moves to 6/1/27. 9/19/24- ISD updated to 2027 per WPL/Greg A via email 12/15/23- per update from Greg A via email, ISD moves to 12/31/28 (Alliant was unable to obtain the land) 11/28/23- PM assigned sent to customer 9/11/23 - CW letter is executed ​6/6/23- ISD moves to 12/31/25​ 4/21/23- ICC email sent to customer with initial CW determination ​4/4/23- LIRF deemed complete and customer notified 6/10/22- per email from Bob G, ISD moves to 2024 03/09/21- ISD moves to 12/31/23 per QP meeting 03/13/19- ISD is 2022 per QP meeting 09/11/17- ISD moves to 12/31/21 12/12/16- Per QP meeting, ISD moves from 12/31/19 to 12/31/20 08/08/16- per Greg via email, ISD moves from 6/1/19 to 12/31/19 09/3/15- per QP meeting, ISD moves form 2017 to 2019 6/2/14 Customer to submit a LIRF for review | Gerdes, Michelle;#930 | Alternative Assessment
2020-11-06 | 2020-11-12 | 40660 | Alliant Energy | Lancaster 138kV | Additional Xfmr | 18 | 2026-08-28 | WPL will install a 138/24.9 kV 33 MVA transformer at the Lancaster Substation to connect to Y-113. Y-113 will become a 25 kV distribution line. ATC will consider retiring the 138/69 kV transformer and 69 kV bus at Lancaster and transfer line Y-113 to Alliant to use as a 25 kV line. ATC will also investigate how to provide bus separation on the 138 kV bus for the 2 Alliant transformers. | 3/14/26- ISN received for the ATC substation scope. Tline scope (retirement of Y113) is pending with the August 2026 ISD. 3/6/25- ISD moves to 3/1/26 per QP meeting. 2/28/24- per QP discussion, ISD moves to 12/31/25 8/16/22- ISD moves to 12/31/24 1/11/22- PM assigned and customer notified 3/22/21- CW letter executed 3/9/21- per QP meeting, ISD moves to 12/31/23 12/10/20- initial customer communication sent to Alliant 11/12/20- LIRF deemed complete and customer notified | Osvatic, Mark;#111 | Alternative Assessment
2020-11-06 | 2020-11-12 | 40661 | Alliant Energy | Lancaster Distribution | Xfmr Repl | 18 | 2025-12-31 | WPL will replace the existing distribution transformer with a 24.9/12.4 kV 15 MVA transformer. Y-113 will become a 25 kV distribution line. ATC scope of work: No Capital Work | 2/28/24- per QP discussion, ISD moves to 12/31/25 1/11/22- PM assigned and customer notified 3/22/21- CW letter executed 12/10/20- initial customer communicatino sent to Alliant 11/12/20- LIRF deemed complete and customer notified | Osvatic, Mark;#111 | NCW - LDC Support
2017-07-21 | 2017-08-04 | 40472 | Alliant Energy | Loganville | Xfmr Repl | 12 | 2030-12-31 | Alliant transformer replacement and sub rebuild on existing land. MCW for ATC new jumpers and insulators to accommodate new dead-end and connect portable sub. | 6/3/25 - per QP meeting, ISD moves to 12/31/2030. 5/12/25 - sent PM assigned email, Bobby Lampshire. 12/20/24- submitted in Exto -PI142 10/15/24- MCW letter sent to customer 8/16/22- ISD moves to 12/31/28 6/15/21- per QP meeting, ISD moves to 12/31/26 1/25/21- Per email from Chris Allen, ISD moves to 2024 6/12/19- ISD moves to 12/31/23 3/13/19- per QP meeting, ISD moves from 2021 to 2022 08/04/17- LIRF deemed complete and customer notified | Lampshire, Robert;#112 | MCW
2021-10-28 | 2021-11-11 | 40730 | Alliant Energy | Mercury Marine | Xfmr Repl | 18 | 2026-08-01 | Mercury Marine to replace their T41 transformer and its supporting equipment (dead end, secondary switchgear, etc.) due to age and capacity limitations. They will also be upgrading their high side protection from fuses to a circuit breaker.As part of the upgrade Mercury looked at a few new site layouts and after some consideration they ultimately settled on relocating the new equipment slightly to the East of where it is today (see attached layout). The ATC scope of work has been narrowed down to the following:ATC to install new jumpers & insulators on the new MM dead-end structure.ATC to relocate STR 62 on line Y-60 to accommodate the relocated T41 dead-end structure (shifted closer to the T-Line pole).ATC to consider relocating STR 63 on line Y-114. This may be needed depending on where STR 62 is moved to and spacing requirements between the two lines entering the substation.ATC to consider developing a plan to connect the Y-60 feed (normally feeds T41) to T42 in the event of an extended outage on Y-114 (normally feeds T42) during the project. This was at the request of Mercury Marine and would only be used for the duration of the project.This stems from the fact that Mercury Marine was concerned that they will be on a single power feed for the duration of the project (~3 months) and an unplanned, extended down would result in costly damage to their equipment. The decision to develop this plan and the extra cost to implement will be up to Mercury Marine.The tentative thought was to implement the plan if an outage occurred that would be a lengthy fix. At that point line Y-114 would be disconnected, then line Y-60 transitioned to the Y-114 poles, and lastly terminate it to T42.A sectionalizing project was dismissed at this location due to space constraints and MM being unwilling to give up any land for the project. The thought is to add sectionalizing breakers at the Morris St. substation in the future instead. | 10/3/25- per update from Nick H, ISD moves to 8/1/26. 3/6/25- ISD moves to 12/1/25 per QP meeting. 9/19/24- ISD update to 9/2025 per WPL/Greg A via email 3/28/24- PM assigned email sent to customer 1/8/24- CW letter executed ​8/31/23- per update from WPL, ISD moves to 4/1/25 ​6/6/23- ISD moves to 12/31/25 8/16/22 - move ISD to 12/31/23 12/9/21- ICC email sent to customer 11/11/21- LIRF deemed complete and customer notified | Pericolosi, Jim;#114 | Alternative Assessment
2025-05-01 | 2025-05-14 | 41135 | Alliant Energy | Morris St | Xfmr Repl | 30 | 2028-12-31 | WPL to rebuild the Morris St substation with a 69 kV high side circuit breaker, a new 69- 26.2/13.09 kV transformer, and a 6-position distribution switchgear. WPL to upgrade the high-side protection from fuses and feeder reclosers to 69kV circuit breakers. WPL requests an additional feeder position. ATC to build a new Morris St Substation with 6 position segmented straight bus, three positions for ATC transmission lines, one position for Alliant distribution and two future positions. ATC to install one bus tie switch with space provisions for a future bus tie breaker and a second bus tie switch.ATC to rebuild 0.2 miles of Y-114 (North Fon du Lac - Mercury Marine) as double circuit 69 kV to service Mercury Marine as a radial load out of the Morris St substation. | 10/23/25 – PM assignment email sent – Erin Cerveny 9/26/25- CW letter executed. 7/7/25- CW letter sent to WPL, pending execution 6/11/25 - initial capital work determination email sent. 5/14/25 - LIRF deemed complete and customer notified 3/12/25- added to potential queue, discuss with Alliant. | Gossen, Erin;#808 | System Study
2024-09-18 | 2024-09-27 | 41037 | Alliant Energy | Neenah Creek | Retirement | 12 | 2026-12-31 | WPL to retire Neenah Creek SS and all distribution assets. Neenah Creek load will be transferred to Oxford SS and future forecasted under Oxford SS. (LIRF #40658) Retirement of Y-181 tapped line section (NCKT-NCK) serving Neenah Creeks SS, including: Replacement of three-way GOAB with tangent structure. Retirement of jumpers and insulators entering Neenah Creek SS. | 6/3/25 - per QP meeting, 12/31/26 retirement. May 2025 - confirmed this is in PM with Oxford project team. 12/20/24- Submitted in Exto in Dec 2024, PI139 10/24/24- MCW letter sent to customer 9/27/24- LIRF deemed complete and customer notified | Ford, Chad;#1103 | MCW
2023-04-10 | 2023-04-24 | 40857 | Alliant Energy | North Fond Du Lac | Xfmr Repl | 24 | 2026-06-01 | WPL to retire the existing T35 transformer. Associated high-side equipment (408-CS) and foundations will remain in place for future 2nd xfmr. WPL to replace the existing T33 transformer with a 138/12.47 kV, 20/26/33 MVA transformer, and also replace the existing 1977-CS circuit switcher with a 138 kV circuit breaker. Alliant will relocate the high side switch (1977-A) to the Alliant dead end structure, and installing new distribution switchgear. ATC Scope - MCW, ATC to install new jumpers & insulators in place of the original 1977-A switch. ATC will install new strain bus and post insulators to Alliant dead end structure and will also install new jumpers and insulators to the connect the new Alliant high side disconnect to the new ATC strain bus. | 9/27/24- ISD moves to 2026 per QP meeting. 6/12/24- per QP meeting, ISD moves to 6/1/26 4/10/24- PM assigned and customer notified. Note - ECI will be managing this project 1/24/24- MCW letter sent to customer 05/22/23- Initial CW determination sent to customer ​4/24/23- LIRF deemed complete and customer notified ​4/5/23- added to potential queue | Lampshire, Robert;#112 | MCW
2025-04-22 | 2025-04-25 | 41130 | Alliant Energy | North Tomah | Sub Rebuild | 12 | 2027-05-31 | WPL to rebuild the North Tomah Sub with a 33 MVA 69/24.9-12.47kV transformer and five circuits distribution bus (four existing circuits with one future). ATC to install new jumpers and insulators and install new static connections to the new WPL dead end structure. | 10/23/25 – PM assignment email sent – Bobby Lampshire 9/17/25 – Per QP meeting, ISD moves up to 5/31/27. 6/3/25 - per QP meeting, ISD moves to 12/31/27 - MCW letter sent to customer on 5/27. 5/27/25 - MCW letter sent to customer. 4/28/25 - deemed complete 4/25/25, customer notified on 4/28/25. | Lampshire, Robert;#112 | MCW
2023-11-17 | 2023-12-06 | 40930 | Alliant Energy | Northgate | Sub Rebuild | 12 | 2025-12-31 | Alliant to rebuild the Northgate substation on the existing site. The low side distribution equipment will be upgraded to a 7 feeder switchgear. Additional SCADA/control capabilities will be added to the substation with the project. The high side equipment and transformer will be left as is. The LIRF notes a portable substation will be required as part of this project. ATC to perform the connection/disconnection of the portable substation. Alliant ownershipdoes not start immediately after the tap structure, our EMS is incorrectly labeled. | 7/15/25- ISN received for X64 rebuild 4/10/24- PM assigned and customer notified 2/28/24- per QP discussion, ISD moves to 12/31/2025 1/9/24- MCW letter and ICC email sent to customer 12/6/23- LIRF deemed complete and customer notified | Lampshire, Robert;#112 | MCW
2020-11-06 | 2020-11-12 | 40658 | Alliant Energy | Oxford | Additional Xfmr | 18 | 2026-10-01 | WPL will install a new 69/12.47 kV 9.375 MVA transformer, distribution feeders, and 2000-amp circuit breaker at the Oxford substation. WPL will retire Neenah Creek transformer, distribution bus, and reroute the distribution feeders to the Oxford Substation. ATC to retire Neenah Creek tap and remove the existing Neenah Creek tap 3-way switch. ATC to expand the Oxford 69kV Bus to north andprovide jumpers and insulators to allow the new WPL transformer to be interconnected to Oxford 69kV bus. | 6/3/25 - per QP meeting, ISD moves to 10/1/26. 3/13/25- PM assigned email sent to customer 12/20/24- Submitted in Exto in Dec 2024, PI139 9/27/24- ISD moves to 12/31/27 per update at QP meeting 9/16/24- CW letter executed 2/28/24- ISD moves to 12/31/26 per QP discussion. 12/4/23- per update from Ryan/Alliant, ISD moves to 12/31/25 1/31/22- per QP meeting, ISD moves to 12/31/26 6/15/21-ISD moves to 12/31/25 per QP meeting 12/10/20- ICC email sent to customer 11/12/20- LIRF deemed complete and customer notified | Ford, Chad;#1103 | Alternative Assessment
2024-03-07 | 2024-04-09 | 40583-1 | Alliant Energy | Pleasant View | Sub Rebuild | 24 | 2028-05-01 | WPL to replace T31 and T32 to 138/24.9kV 30/40/50 MVA rated transformers along with the associated switchgear. WPL will replace the circuit switchers to circuit breakers on 138kV sides for T31, T32 and T33. WPL will relocate ATC’s and WPL’s relay connections to the new breakers. (Described in B2-N16112C one line diagram page of the attached project binder) System Protection team needs to review and verify if they agree with this. ATC will consider providingnew jumpers and insulatorsfor the new disconnect switch on high side of T31 and T32. No physical scope expected for ATC on high side of T33.Modify existing ATC bus differential relays on bus 1 and bus 2 to terminate into the new breaker CTs | 12/9/25: Per QP Meeting, ISD moves to 5/1/28 ​8/14/24- PM assigned and customer notified. Will be managed by ECI staff, with oversight from Bobby Lampshire. 5/7/24- MCW letter and ICC sent to customer 4/9/24- LIRF rev deemed complete and customer notified ​​4/5/23- ISD moves to 12/31/26 8/16/22- ISD moves to 12/31/25 2/5/21- ICC and MCW letter sent to customer 12/1/20- per QP meeting, ISD moves to 12/31/24 9/9/19- LIRF deemed complete and customer notified | Lampshire, Robert;#112 | MCW
2024-05-01 | 2024-05-17 | 40981 | Alliant Energy | Potosi | Retirement | 12 | 2025-12-31 | WPL will retire Potosi interconnection once Tennyson is in service and all feeders Potosi feeders cut over to Tennyson. ATC to install a few 138 kV transmission line pole on the Nelson Dewey – Tennyson 138 kV line (X-15) to allow the retirement of the existing Potosi tap structure (STR 128) and Potosi tap conductor. | 12/30/25- ISN received for Potosi DIC, confirm with WPL this project is complete. 10/24- Assigned to contract PM- Christopher Fredrick with oversight from Bobby Lampshire. 9/19/24- ISD moved to 2025 per email from WPL/Greg A 5/22/24- PM assigned and customer notified 5/17/24- LIRF deemed complete and customer notified | Lampshire, Robert;#112;#Frederick, Christopher;#880 | Alternative Assessment
2023-09-13 | 2023-09-27 | 40893 | Alliant Energy | Poynette | Xfmr Repl | 24 | 2027-12-31 | Alliant to rebuild the existing Poynette Substation in place. The rebuild appears to be a one for one replacement of the existing equipment at this point. LIRF lists that Alliant will be providing a portable substation as part of the project. ATC to perform the connection on the portable substation. ATC to install new jumpers & insulators on the Alliant dead end structure. ATC to relocate the existing Poynette tap switch, see the project notes section for reasoning. The relocation involves retiring the existing Poynette tap switch structure, installing a new Poynette tap switch structure, installing six new T-Line poles, and installing the necessary conductor (~ 0.26mi) for the reroute. | 3/6/25- ISD moves to 12/31/27 per QP meeting. 10/24- PM reassigned, Theodore Tolish (contract PM) with oversight from Bobby Lampshire 6/12/24- per QP meeting, ISD moves to 4/30/27 6/7/24- PM assigned and customer notified- S&L will PM with oversight from Mark Osvatic 5/6/24- CW letter executed 2/28/24- ISD moves to 2027 per QP meeting 10/27/23- ICC email sent to customer. CW letter to be executed at later date. 9/27/23- LIRF deemed complete and customer notified ​8/16/22- added to potential project per D-T Check In Meeting | Lampshire, Robert;#112;#Tolish, Theodore;#1006 | Alternative Assessment
2016-08-10 | 2016-08-19 | 40397-1 | Alliant Energy | South Lake Geneva | Additional Xfmr | 24 | 2026-06-01 | New ATC jumpers | 6/3/25 - per QP meeting, ISD moves to 6/1/26. 2/28/24- per QP discussion, ISD moves to 12/31/26 8/16/22- ISD moves to 12/31/27 1/31/22- per Greg A, ISD moves to 12/31/25 09/15/20 - per QP meeting, ISD moves to 12/31/24 10/9/19- per QP meeting, ISD moves to 12/31/23 08/19/16- LIRF Rev 1 deemed complete and customer notified 08/08/16- per Greg's via email ISD moves from 10/01/17 to 12/31/22 08/02/16- transitioned to Project Management, customer notified 04/19/16- MCW determination letter was emailed to the customer 03/03/16- LIRF deemed complete and customer notified | Hanold, Nick;#102 | MCW
2024-08-08 | 2024-08-14 | 41022 | Alliant Energy | Spring Brook | Sub Rebuild | 12 | 2028-06-30 | Alliant is planning to replace their Spring Brook transformer and build a five-circuit overhead distribution bus. They plan to retire their current assets and install the new equipment in the same location as the old equipment. ATC will need to re-jumper to the new transformer in the same location as the existing transformer. | 3/27/26 – Per email updates from Nick H, ISD moves to 6/30/2028 5/9/25 - PM assigned email sent - Bobby Lampshire. 12/20/24- Submitted in Exto in Dec 2024, PI143 9/13/24- MCW letter sent to customer 08/14/24- LIRF deemed complete and customer notified | Lampshire, Robert;#112 | MCW
2021-11-05 | 2021-11-19 | 40737 | Alliant Energy | Stoughton | Retirement | 18 | 2027-12-31 | Alliant wants to retire transformer T41 and all associated distribution equipment at the Stoughton Substation. ATC will consider retiring the jumpers going into switch 695-A. | 12/09/24- per WPL, ISD moves to 12/31/27 5/17/24- PM assigned and customer notified 4/22/24- PR submitted 12/14/21- ICC and MCW letter sent to customer 11/19/21- LIRF deemed complete and customer notified | Hughes, Patrick;#1011 | MCW
2023-11-03 | 2023-11-17 | 40924 | Alliant Energy | Sunrise | Additional Xfmr | 18 | 2029-12-01 | Alliant submitted this LIRF for a proposed expansion at the Sunrise substation. Alliant plans to install a second transformer (138/24.9kV 20/33MVA) and distribution bus off the future open position at the Sunrise substation.LIRF lists project drivers to be high loading on the existing Sunrise transformer and difficulty bridging the entire peak load when the transformer is out of service. Alliant also plans to upgrade the high side protection on the existing T31 transformer from a circuit switcher to a breaker. LIRF notes ongoing coordination between ATC & WPL for the MISO J1460 solar project at Sunrise.The J1460 solar project involves ATC 138kV bus work and is when the additional 138kV terminal will be added.Alliant plans to complete the installation of the new equipment during or after the J1460 project wraps up.At a minimum Alliant would like to perform the breaker upgrade on the existing equipment and install the high side switch for the new equipment during the J1460 bus work outage. ATC to install new jumpers & insulators to the new Alliant breaker. ATC to install new jumpers & insulators to the new Alliant switch. ATC to consider installing a firewall between the existing ATC control house and the existing WPL transformer #31.When Alliant first floated the project Chris Glauser reached out internally to note the distance between the two pieces of equipment is only ~12’ and could warrant a firewall for protection.As mentioned above, the addition of a 138kV terminal is included in the J1460 scope of work. | 3/27/26 – Per email updates from Nick H, ISD moves to 12/1/29 5/12/25 - sent PM assigned email, Bobby Lampshire 2/26/25- CW letter executed 12/18/23- ICC email sent to customer. CW letter to follow at a later date. 11/17/23- LIRF deemed complete and customer notified | Lampshire, Robert;#112 | Alternative Assessment
2023-09-13 | 2023-09-27 | 40892 | Alliant Energy | Tomah Industrial Park | New Sub | 24 | 2026-05-01 | WPL to retire the existing Tomah Industrial Park substation. WPL to construct a new Tomah Industrial Park substation to the west of the existing site, and install a 33 MVA, 69/24.9-12.47 kV transformer. Five overhead distribution feeders will exit the low-side bus. ATC will retire the existing 32a dead-end structure. ATC will install a new dead-end structure to terminate into the new Tomah substation. ATC will provide jumpers and insulators to terminate into the WPL dead-end structure within the substation. | 9/19/24- ISD moves to 5/26 per WPL/Greg A via email 5/29/24- PM assigned and customer notified. Will be managed by ECI, with oversight from Bobby L 4/26/24- MCW letter sent to customer 2/28/24- per QP discussion, ISD moves to 12/31/26 10/27/23- ICC email sent to customer. Capital work letter to be executed at a later date. 9/27/23- LIRF deemed complete and customer notified 8/16/22- added to potential queue to D-T queue check in​ | Lampshire, Robert;#112 | Alternative Assessment
2021-04-13 | 2021-04-27 | 40696 | Alliant Energy | Vienna | Additional Xfmr | 18 | 2026-12-31 | Alliant plans to add a 138/25/12.47 kV, 20/26/33 MVA transformer with a high-side circuit breaker at the Vienna Substation. Alliant also plans to replace the high-side circuit switcher on the existing transformer with a circuit breaker. ATC will consider installing line breakers, providing new jumpers/insulators for the transformer addition, and support for a portable substation. | 12/13/23- per email from Greg A, ISD moves to 12/31/26 ​6/29/23- PM assigned and customer notified ​4/28/23- CW letter executed 8/16/22- ISD moves to 12/31/25 5/15/21- ICC email sent to Alliant 4/27/21- LIRF deemed complete and customer notified | Nyman, Garrett;#757 | Alternative Assessment
2023-12-19 | 2024-01-16 | 40948 | Alliant Energy | West Towne | High Side Protection Replacement | 18 | 2029-12-31 | Alliant to replace their West Towne substation switchgear. This is being done to prepare for the conversion of the distribution system to 24.9kV (currently 13.1kV). Alliant will also upgrade their high side protection from a circuit switcher to a breaker and disconnect. LIRF notes that due to space constraints, ATC bus modifications will be required to accommodate the new breaker and disconnect. The existing transformer will be kept as part of this project. ATC to perform the connection & disconnection of the portable substation. ATC to rebuild the bus on the Alliant section of the substation. The high and low sections of bus will be swapped so that the “loop through” section is high and the “distribution tap” section is low. It will then match the other two MGE sections upon completion. The “tap section” will be shifted North slightly to better align with the new breaker. Further review should be done on the C-phase angled transition to verify the bus/disconnect clearances are sufficient. ATC to replace the disconnect switches on either side of the bus section being worked on. ATC to relocate the bus PTs to match the “tap section” shift North. ATC to install new jumpers & insulators to the new Alliant disconnect switch. ATC to consider repairing/replacing the bus foundations as the LIRF notes there is some deterioration going on. ATC to consider performing a LiDAR scan of the substation to verify drawing dimensions are accurate given the tighter clearances. | 3/27/26 – Per email updates from Nick H, ISD moves to 12/31/29 5/12/25 - sent PM assigned email, Paulo Pavelski 05/07/25- CW letter executed 9/19/24- revised ISD provided by Greg A via email 2/28/24- per QP discussion, ISD moves to 12/31/27 2/15/24- Initial CW determination email sent to customer. CW letter to follow. 1/16/2024- LIRF deemed complete and customer notified | Pavelski, Paulo;#931 | Alternative Assessment
2023-06-29 | 2023-06-30 | 40722-1 | Black Earth Utilities | Black Earth Substation | Additional Xfmr | 36 | 2026-06-01 | BEEU will install one 69/12.47 kV 7.5/10.5 MVA transformer with either power fuses or a transruptor at the existing Black Earth substation. ATC scope of work:ATC will install a new dead end structure with a three way set of disconnect switches to interconnect the new 2nd BEEU transformer. ATC will reroute the Y-62 line around the north of the existing Black Earth Substation, with the intent to terminate into the existing STR 118297 dead end structure on the east side of Blue Mounds st. | 11/26/25- ISN received for ATC scope. Confirm if 6/1/26 is the ISD for the Black Earth scope. 9/11/25 – Per meeting, ISD moves up to 6/1/26 5/5/25- per project team notes, ISD moves to 11/1/26 3/25/25 - ISD is sometime in Fall 2025, per Forster meeting. 2/1/24- PM assigned email sent to customer 12/5/23- PR submitted 12/1/23- CW letter fully executed 9/8/23- BEEU provided updated information, including ISD, via LIRF. LIRF not treated as a revised LIRF. ​7/13/23- ICC email wiith CW determination sent to customer. CW letter to follow for rev 1 06/30/23- LIRF rev1 deemed complete and customer notified 10/19/21- ICC email with CW determination sent to customer 9/22/21- LIRF deemed complete and customer notified | Pavelski, Paulo;#931 | Alternative Assessment
2024-06-13 | 2024-06-26 | 40996 | BPMA | East Shawano | Xfmr Repl | 18 | 2027-11-01 | BPMA to install a new second transformer at East Shawano 69kV substation Bus 5. The new transformer will have the same MVA rating as the existing one (25/33.3/41.7 MVA 55-degree rise and 28/36.7/46.7 MVA 65-degree rise) BPMA to keep the existing transformer as an energized reserve without any load. ATC to install a second bus tie disconnect switch between Bus 4 and Bus 5 with space provision for a circuit breaker. ATC to install new jumpers and insulators to BPMA high side disconnect for the new transformer. ATC to perform necessary protection modifications to support an additional distribution transformer. | 5/12/25 - sent PM assigned email, Bobby Lampshire 3/25/25 - ISD updated via Forster meeting 8/9/24- MCW letter sent to customer 6/26/24- LIRF complete and customer notified | Lampshire, Robert;#112 | MCW
2024-12-20 | 2025-01-07 | 41071 | Brodhead Water ＆ Light | Brodhead Muni 1 | Retirement | 12 | 2025-06-01 | Brodhead has completed a significant portion of conversion away from 4 kV. Brodhead will decommission the Muni 1 Substation. Brodhead is requesting to take ownership of the wood transmission pole outside the substation after removal of 69 kV line, since Brodhead has under-built distribution infrastructure.. ATC will de-energize and remove the transmission tap that serves this substation. (except structure 2A) ATC to file abandonment application with PSCW ATC to transfer ownership of structure 2A to Brodhead. Due to the timeframe requested by the customer and required abandonment application, Forester agreed to open the high-side switch at the station which would allow Brodhead to remove their equipment prior to ATC’s abandonment. | 3/25/2025 - Subs are deenergized. ISD reflecting decomissiong and ATC abandonment process 3/13/25- PM assigned email sent to customer January 2025- added in Exto - PI151 01/28/25- MCW letter sent to customer 1/7/25- LIRF deemed complete and customer notified | Gerdes, Michelle;#930 | MCW
2024-12-20 | 2025-01-07 | 41072 | Brodhead Water ＆ Light | Brodhead Muni 2 | Retirement | 12 | 2025-06-01 | Brodhead has completed conversion away from 4 kV. Brodhead will decommission the Municipal Substation 2 transformer. Brodhead will remove the transformer, and other distribution equipment. The substation steel structures will remain in place for potential future use. There are no current plans to utilize the site, but it will retained for future use. ATC will de-energize and remove the transmission tap that serves this substation. ATC to file abandonment application with PSCW Due to the timeframe requested by the customer and required abandonment application, Forester agreed to open the high-side switch at the station which would allow Brodhead to remove their equipment prior to ATC’s abandonment. | 3/25/2025 - Subs are deenergized. ISD reflecting decomissiong and ATC abandonment process 3/13/25- PM assigned email sent to customer January 2025- added in Exto - PI151 01/28/25- MCW letter sent to customer 1/7/25- LIRF deemed complete and customer notified | Gerdes, Michelle;#930 | MCW
2024-11-26 | 2024-12-04 | 41059 | Central Wisconsin Electric Cooperative | Central | New Sub | 24 | 2026-04-01 | Central Wisconsin Electric Cooperative will install a new 69 kV to 7.2/12.47 kV substation. The anticipated site is on CWEC property just off Lystul Road which would be approximately 0.3 miles from an existing ATC 69 kV transmission line.. ATC Scope of Work: Install 3-way GOAB switch structure with whips near Y-71 structure 99. Route approx. 0.5 miles of new 69kV line to new SS location. | 5/9/25 - PM assigned email sent - Dustin Johanek. 3/17/25 - moved to SRA program, PM to be assigned. Kaylin to send email to customer once PM available. 2/13/25- CW letter executed Entered into Exto - PI148 2/7/25- CW letter sent to CWEC for execution 1/3/25- ICC email sent to customer, CW letter to follow. 12/4/24- LIRF deemed complete and customer notified | Johanek, Dustin;#107 | Alternative Assessment
2022-10-17 | 2022-10-31 | 40816 | Cloverland Electric Cooperative | Manistique Pump Station | Xfmr Repl | 18 | 2026-09-01 | CEC will relocate substation due to age and condition of the existing transformer and a desire to move outside of the Enbridge Fence.The new substation will include a new 69/4.16 kV 7.5 MVA transformer to provide dedicated service to Enbridge. ATC will remove two transmission towers (146481-146482) and consider installing a single 69kV dead end, as well as terminate jumpers into the new substation. | 8/25/25- ISD moves to 9/1/26 per update from Brian L. 10/15/24- per discussion with CEC - ISD will be 3/1/25, possibly closer to May 2025 - TBD. 10/26/23- PM assigned email sent to customer ​11/30/22- ​CW determination and ICC response sent to customer 10/31/22- LIRF deemed complete and customer notified | Pericolosi, Tony;#701 | MCW
2023-02-07 | 2023-02-21 | 40812-1 | Cuba City Water & Light | Cuba City - Monroe Street | Additional Xfmr | 24 | 2025-12-31 | Cuba City to install 2nd distribution transformer at Cuba City South (Monroe St.) and requesting half of loop-through high side bus be constructed with Phase 1. Phase 2 will complete loop-through bus configuration. ATC will consider installing half of a loop-through 69 kV straight bus associated with the installation of Cuba City’s 2nd transformer. Initial bus installation to leave provisions for future 69 kV line breaker. Future state is 69 kV loop-through straight bus with 2 line breakers and space for a bus-tie breaker. ATC will consider replacing existing 69 kV line from Roaster Road to the existing Cuba City Monroe St Substation with a double circuit line to prepare for Phase 2. | 10/9/25- per update from Jim Z, ATC has completed construction for Phase 1, Cuba City might have some additional work before they can energize their transformer. There is an outage with a Hold Card on the switch associated with the 2nd transformer until 12/30/2025 (25-0214Cuba City might have some additional work before they can energize their transformer. There is an outage with a Hold Card on the switch associated with the 2nd transformer until 12/30/2025 (25-02145) Phase 2 construction will be in 2027. 5) Phase 2 construction will be in 2027. 9/29/25- ISN received for the Cuba City South Expansion. 2/12/24- PM assigned email sent to customer 12/6/23- PR submitted 12/5/23- CW letter for phase 1 & 2 executed 9/25/23- CW letter executed ​3/21/23- ICC email with CW determination sent to customer ​02/21/23- LIRF rev 1 deemed complete and customer notified ​11/15/22- CW assessment/ICC sent to customer 10/18/22- LIRF deemed complete and customer notified | Nyman, Garrett;#757 | Alternative Assessment
2025-02-24 | 2025-02-25 | 40881-2 | Evansville Water ＆ Light | Union Townline Substation | Additional Xfmr | 24 | 2027-03-01 | ​WPPI/Evansville Water & Light to install a second 69/12.47kV 12/22.4MVA transformer at the Union Townline Substation (UTL). A circuit switcher will be installed for high side protection. Low side bus, feeder terminals, and a bus tie switch (load break) will be installed. ATC to install approximately 0.08 miles of 69kV line to tie the new transformer to Y-158. ATC to install a new dead end structure in the substation for the new line. ATC to install a new high side loop through bus configuration. ATC to install line breakers and associated control house and provisions for a future bus tie breaker. ATC to remove the existing Union Townline Tap (UTLT) three way switching structure. ATC to relocate the dead end structure of the existing substation feed to make room for the new high side bus and sectionalizing equipment. | 4/4/25- CW rev2 executed by ATC and Evansville 2/25/25- LIRF rev2 deemed complete and customer notified. 1/30/25- Evansville received CA approval from PSCW for load addition 12/27/24- transitioned to PM 10/3/24- CW letter executed 9/16/24- CW letter rev1 sent for execution to Evansville. 5/15/24- ICC email sent to customer. CW letter rev1 to follow. 4/17/24- LIRF rev1 deemed complete and customer notified 4/8/24-CW letter executed 11/10/23- Nick discussed equipment lead time issues with customer. ISD moved to 5/1/26 with approval from customer ​8/21/23- ICC email with CW determination sent to customer ​7/26/23- LIRF deemed complete and customer notified | Groeschel, Wayne;#1102 | Alternative Assessment
2025-04-09 | 2025-04-15 | 41120 | Madison Gas ＆ Electric | Huiskamp | Xfmr Repl | 12 | 2027-06-01 | MGE to replace Transformer 1 and Transformer 2 with new 138/69kV-13.8kV 20/37 MVA transformers at Huiskamp. Transformer 1 will be moved to the open 69kV bay on Bus 1. Transformer 2 will be replaced in its current location on Bus 2. MGE to install a new 2000A enclosed switchgear and 20/37 MVA power transformer connecting to the new Transformer 1. ATC to install new jumpers and insulators to accommodate the new high-side disconnect switch on Transformer 1. | 11/26/25: PM assigned email sent – Jason Nett 5/13/25 - MCW letter sent 4/16/25 - LIRF deemed complete 4/14 and customer notified on 4/15. 3/18/25- added to potential queue | Nett, Jason;#1101 | MCW
2023-09-19 | 2023-10-04 | 40896 | Mazomanie Electric Utility | Mazomanie West | Additional Xfmr | 18 | 2026-06-01 | Mazomanie to install a second transformer (69/12.47kV, 15/20/25MVA) and the supporting LDC owned bus/equipment at the Mazomanie West substation. The primary need driver here is to improve redundancy and reliability by having a backup transformer. Per the LIRF, Mazomanie can no longer transfer the entire load from the existing transformer in the event of maintenance or an outage. ATC to install new insulators on both the existing ATC open terminal dead-end structure and the new Mazomanie dead-end structure and then install T-Line/jumpers to connect the two. | 9/11/25 – Per meeting, ISD moves to 6/1/26 3/25/25 - ISD is sometime in Fall 2025, per Forster meeting 4/11/24 - PM assigned, will be project managed by ECI 11/7/23- MCW letter sent to customer 10/4/23- LIRF deemed complete and customer notified | Lampshire, Robert;#112 | MCW
2022-11-10 | 2022-11-29 | 40682-1 | Plymouth Utilities | Plymouth #5 | New Sub | 36 | 2025-09-01 | Plymouth Utilities will construct a new Plymouth #5 Substation near the intersection of County Roads A and V to support the expansion of the ANR Pipeline facility. ATC will facilitate a BVP study process. ATC will consider constructing a new double circuit 138 kV line (approx. 5 to 7 miles) to loop through Plymouth's new substation. | 9/11/25- We left the ISD as 9/1/2025, since that was the customer requested ISD. The current ATC ISD is 6/1/2026. 6/27/25- transformer test report shared for one of the new xfmrs. 9/28/23- BVP executed ​​4/17/23- PM - Mark Osvatic - has been assigned as a part of the enhanced scoping effort, PM assigned email sent to customer 12/29/22- CW determination/ICC email sent to customer 11/29/22- LIRF rev 1 deemed complete and customer notified 3/17/21- ICC email sent to customer 2/17/21- LIRF deemed complete & customer notified | Mainwaring, Kyle;#119 | Alternative Assessment
2024-12-02 | 2024-12-17 | 40760-1 | Reedsburg Utility Commission | Artesian | Other |  | 2026-12-31 | Reedsburg Utility Commission (RUC) is planning to rebuild RUC-owned 69 kV circuit Y-162 from Webb Substation to the Grede West switch R6920-A. Updated from CW letter: ATC to construct approximately 0.26 miles of 69 kV line to bypass the Reedsburg Substation for line Y-53 (Loganville – Artesian). • ATC to construct a new 3-way GOAB with 3 manual load break switches on Y-53. • ATC to construct approximately 0.09 miles of 69 kV line to connect line Y-53 to Y-305 (Artesian - Webb Avenue 69 kV). • ATC to retire line Y-162 (Artesian – Reedsburg) & retire the Reedsburg substation. o ATC to file a PSCW abandonment application for the retired facilities. • ATC to retire portions of line Y-53. o ATC to file a PSCW abandonment application for the retired facilities. • RUC to reroute line Y-305 to the line terminal for breaker 2394-S at Artesian. • RUC will operate switch R6955-LB on Y-305 as normally closed. • ATC to replace jumpers for line Y-305, attaching to the dead end for breaker 2394-S. • ATC to retire breaker 2397-S and switch 2397-L at Artesian substation. • ATC to construct a new 3-way GOAB with 3 manual load break switches at the Webb Ave tap on Y-305. | 9/11/25 – Per meeting, ISD moves to 12/31/26 4/9/25- CW letter executed for full reconfiguration project of the Reedsburg system. Includes retirements. 3/25/2025 - ISD updated to match project schedule 12/17/24- LIRF rev1 has been reviewed, deemed complete and customer is notified. LIRF will not be rerouted as there is a project team already working on this scope. The revised LIRF is for documentation purposes. ​8/3/23- ISD updated to 9/1/24 per internal discussions. 1/31/23- per update from Crystal, ISD moves to end of 2023, may push into Q2 2024. Check in later in year. ​3/15/22- PR 8949 submitted for related Reedsburg retirement projects (ATC only) 3/9/22- TIRF information moved to LIRF form and communicated to customer. Artesian project information is now housed on D-T queue and in LIRF folders (previously submitted via T-T interconnection process 1/11/22- PM assigned and customer notified. 11/5/21- MCW letter provided to customer. 3/11/21- TIRF deemed complete and customer notified. | Pericolosi, Tony;#701 | Alternative Assessment
2022-04-08 | 2022-04-22 | 40768 | Rock Electric Cooperative | Johnstown | New Sub | 24 | 2026-03-31 | REC will construct a new 138 kV substation with one 138/24.9 kV 15/25 MVA transformer with either a circuit switcher or circuit breaker for H-S protection. ATC will consider constructing a new 138 kV loop through straight bus on line 4434 with 2 line breakers and space provisions for a future bus-tie breaker. | 11/8/24- PM reassigned email sent to customer ​5/14/24- ISD moves to 3/31/26 due to material delays. 1/31/23- PM assigned email sent to customer 05/20/22 ICC email with CW determination emailed to customer. 04/22/22- LIRF deemed complete and customer notified | Nett, Jason;#1101 | Alternative Assessment
2025-08-13 | 2025-08-27 | 41166 | UMERC | Strawberry Hill | Xfmr Repl | 12 | 2026-09-01 | UMERC to replace T6 with a base 8.4 MVA transformer. UMERC to utilize a mobile substation to keep customers energized during construction. ATC to support the installation of the mobile substation. UMERC is requesting the mobile substation be installed outside of the Iron Grove Substation. | 12/1/25: PM assignment email sent, Bobby Lampshire 10/2/25 - ISD updated to 9/1/26 9/25/25 – MCW letter sent 8/27/25 - LIRF deemed complete, customer notified | Lampshire, Robert;#112 | MCW
2025-01-28 | 2025-02-11 | 41085 | Upper Peninsula Power Company | CR480 Substation | New Sub | 30 | 2027-01-01 | UPPCO to construct a new CR480 substation tapping off of the Huron – Empire 138kV line (X-119). UPPCO to construct a new substation with one new 138/12.5 kV, 5 MVA transformer with a high side circuit breaker for transformer protection. ATC to install three sets of 138 kV horizontal mounted line disconnect switches with super whip. ATC to extend a radial tap approximately 0.1 miles from the existing X-119 line to the new UPPCO CR480 Substation. | 12/11/25 – PM assigned email sent, Travis Steinbrecher 9/30/25 – Per Fall Planning meeting, ISD moves to 1/1/27 7/25/25- CW letter executed 3/11/25- ICC with initial capital work determination sent to customer 2/11/25- LIRF deemed complete and customer notified | Steinbrecher, Travis;#1130 | Alternative Assessment
2022-12-06 | 2022-12-20 | 40835 | Upper Peninsula Power Company | Delta | Xfmr Repl | 18 | 2025-10-01 | UPPCO will replace the Bank 1 transformer with a 69/12.47 kV, 12/14/16 MVA transformer UPPCO will also replace the high-side disconnectswitch, and replace existing fuses with a high-side breaker (similar configuration to Bank 2). ATC will consider installing new jumpers and insulators to the new UPPCO 69 kV high-side disconnect switch, and modify the ATC bus protection with the new high-side breaker. | 11/5/25 – xfmr test report received. 5/8/25 - per QP meeting, ISD moved to 10/1/25. ​04/05/23- per UPPCO, ISD moves to 9/1/25. Logan alerted PM Jim P. ​2/22/23- PM assigned and customer notified ​1/23/23- MCW letter sent to customer 12/20/22 - LIRF deemed complete and customer notified 5/9/22 Per QP meeting ISD updated to 12/31/22 5/8/20- added as potential project per Tim K | Pericolosi, Jim;#114 | MCW
2023-12-14 | 2024-01-02 | 40947 | Upper Peninsula Power Company | Timber Products | Load Addition | 0 | 2025-11-01 | A third party customer is planning an operational expansion which will add ~2.4MW of load to the Timber Products substation. The actual MVAR demand/power factor are still unknown, but LDC states they will discuss potential power factor correction with the customer. The load addition includes several motors; the largest is 150HP and will be on a VFD, the largest that will potentially be started across the line is 100HP. At this time UPPCO plans to add fans to their existing transformer to increase capacity to support the added load. ATC Scope of Work: A preliminary review by Michael B. found thermal issues in the area for two N-1-1 scenarios. The thermal issues were driven primarily by low voltages. Both were resolved with the completion of the Munising Statcom (2026 ISD). Temporary mitigation issues are still being discussed. Note the review included the proposed 2.5MW load addition at KI Sawyer (ISD 3/1/2024). ATC to install a mobile capacitor bank to support the added load until the Munising Area Reactive Power Project (MTEP Project ID 19966) is placed in service, targeted for January 2026. | 9/30/25 – Per Fall Planning meeting, ISD moves to 11/1/25. 5/8/25 - per QP meeting, moving ISD to 8/1/25 because customer needed it pushed back. 2/21/25- per update from Jason S at UPPCO, elective facilities work will not be pursued at this time. 10/2/24- per update at QP meeting, ISD moves to end of Q1 2025. 9/4/24- ISN received for mobile cap bank at Munising. 5/30/24- PM assigned and customer notfied 4/18/24- MCW letter sent to customer 1/2/24- LIRF deemed complete and customer notified | Siegler, Dorn;#116 | MCW
2025-01-31 | 2025-02-25 | 40522-2 | Waupun Utilities | Waupun Business Park | New Sub | 18 | 2028-12-31 | Waupun will construct a new substation with one new 69/12.47 kV, 13.5/22.5 MVA transformer with high-side circuit breaker. Waupun will relocate the existing Comtech transformer to Wilson St. Substation. ATC will install line disconnect switches and bus-tie disconnect switches. ATC will reserve space for future install of 2 line breakers, 2 bus disconnect switches, 1 bus-tie breaker and a second 69/12.47kV transformer. ATC will retire the existing Comtech Tap and Waupun South Tap. Remove switch but pole can remain per ATC maintenance. ATC to file PSCW abandonment application. | 9/11/25 – Per meeting, substation name change to Waupun Business Park Substation 5/9/25 - PM assigned email went out - Michelle Gerdes. 3/25/25 - ISD updated via Forster meeting 3/18/25- CW letter executed 2/25/25- LIRF rev2 was deemed complete and customer notified 9/17/24- ICC email sent to customer for rev1 8/19/24- LIRF rev1 deemed complete and customer notified 1/8/23- LIRF revision will be submitted soon. Load addition - 12 MWs (not a data center- Linde/gas processing site). 10/7/21- ISD moves to 12/31/23 per discussions with Waupun and ATC planning 4/17/21- per update from Waupun, keep on in-active tab 9/30/20- ISD updated to 6/1/22 per Jim Z (18 month lead). ISD is technically TBD 5/20/20- per Steve Brooks, this project should remain on the queue 6/10/19- per Customer, project is on-hold indefinitely 07/09/18- LIRF deemed complete and customer notified | Gerdes, Michelle;#930 | System Study
2024-11-06 | 2024-11-20 | 41057 | We Energies | Lyndon | Additional Xfmr | 12 | 2027-05-31 | WEC to install a second 138-24.9kV transformer (T8) and PDC (bus 8 & 9). The high-side bus will be extended for the new transformer along with a new high-side 145kV circuit breaker and disconnect switch. WEC will vacate existing control house and move to new PDC. Existing T9 will remain, but all low-side equipment will be removed and replaced with the subsequent PDC. Existing western gate and driveway will be moved east to allow for convenient entry/exit of the substation ATC to install jumpers/rigid bus to connect to customer-owned switch for T8 | 12/1/25: PM assignment email sent, Bobby Lampshire 12/20/24- MCW letter sent to customer 11/20/24- LIRF deemed complete and customer notified 3/13/24- Per QP meeting, ISD moves to 6/1/27. 3/4/21- ISD moves to 12/31/26 (was 2024 12/11/20- added per qp meeting | Lampshire, Robert;#112 | MCW
2025-09-24 | 2025-10-16 | 41177 | Wisconsin Public Service | Bowen St | Additional Xfmr | 12 | 2027-12-31 | WPS to install a second 69-24.9 kV 26/30 MVA transformer at Bowen St Substation. WPS to install a 69 kV high side disconnect switch, a 69kV circuit switcher, and additional associated distribution feeder equipment. ATC will accommodate the connection of the new WPS high-side switch with specific design details to be finalized during detailed engineering. This scope may involve a modification of bus and/or installation of new jumpers and insulators to the new high side switch.If required, ATC will provide support for the connection and disconnection of a portable substation | 2/18/26- PM assigned email sent, Garrett Nyman 11/14/25- MCW letter sent to customer 10/16/25 - LIRF deemed complete, customer notified | Nyman, Garrett;#757 | MCW
2025-08-14 | 2025-08-28 | 41102-1 | Wisconsin Public Service | Brusbay | Xfmr Repl | 9 | 2026-07-01 | WPS to install a new 69-24.9 kV base 12 MVA transformer, remove existing transformer, replace existing RTU with new RTU panel on ATC Fiber connection, associated feeder equipment upgrades, and replace HVAC. ATC to bring fiber into the Brusbay control house for a fiber connection to the new WPS RTU. ATC to consider installing an ATC owned RTU at Brusbay to control the ATC MODs at Brusbay. | 3/4/26- ISD moves to 7/1/26 12/16/25 – PM assigned email sent, Erin Cerveny 9/26/25 – MCW letter sent 8/28/25 – LIRF rev1 deemed complete, customer notified 4/11/25- NCW letter sent to customer 3/14/25- LIRF deemed complete and customer notified | Gossen, Erin;#808 | MCW
2025-03-07 | 2025-03-21 | 41107 | Wisconsin Public Service | Clear Lake | Xfmr Repl | 18 | 2026-10-01 | WPS to replace Bank 2 transformer with a new base 12 MVA 115-24.9 kV transformer. WPS to upgrade Feeder 242 & 243 protective relays and reclosers, upgrade Feeder 241 voltage regulators and install circuit switchers to the high-side of Bank 1 and Bank 2 transformers. ATC to install new jumpers and insulators to support installation of high-side circuit switchers for Bank 1 and Bank 2 transformers. | 10/2/25 - ISD updated to 10/1/268/15/25 – PM assigned email sent, Bobby Lampshire 6/4/25- WPS will be utilizing contract engineering - Dashille - for this project. Construction will be July - September 2026. 4/18/25- MCW Letter sent to the customer 3/21/25- LIRF deemed complete and customer notified | Lampshire, Robert;#112 | MCW
2024-12-30 | 2025-01-15 | 40863-1 | Wisconsin Public Service | Dunn Road | Xfmr Repl | 0 | 2026-06-01 | WPS is proposing to replace existing distribution transformer bank 1 with a new 69/24.9 kV, 26/30 MVA unit. A new high-side disconnect switch (199) will be installed on its own structure. The existing circuit switcher (199) will be removed and a new 69kV gas circuit breaker will be installed. ATC to extend 69 kV bus and install jumpers to connect to customer owned switch for new Bank 1 transformer | 3/10/25- PM assigned and customer notified 2/13/25- entered into Exto - PI155 2/13/25- CW letter executed by WPS 2/7/25- CW letter sent to WPS for execution 1/15/25- LIRF rev1 deemed complete and customer notified 2/14/23 - Notified by Drew Bain that Dunn Rd XFRM replacement work has moved back up into 2025, change ISD to 12/1/25. 12/4/23- ISD moves to 12/1/27 per QP meeting ​06/16/23- NCW letter and ICC sent to customer ​05/22/23- LIRF deemed complete and customer notified 6/9/22- ISD moves to 12/1/25 per QP meeting 2/26/20- Added to potential queue per QP meeting | Nett, Jason;#1101 | Alternative Assessment
2025-10-01 | 2025-10-15 | 41176 | Wisconsin Public Service | East Krok | Xfmr Repl | 12 | 2026-10-01 | WPS to replace the existing transformer T2 at East Krok with a new 69/24.9kV 22.4 MVA unit with a 69kV circuit breaker for high side protection and install a new 299 switch relocated to a new switch stand. WPS to install a new control house, and complete associated distribution equipment upgrades. WPS will utilize a portable substation to support this project. ATC to install new jumpers and insulators to accommodate the move of the 299 switch to a new switch stand.ATC will provide support for the connection and disconnection of a portable substation. | 3/4/26- ISD moves to 10/1/26 1/29/26 – PM assigned email sent, Dustin Johanek 12/2/25 – per QP meeting, ISD moves to 9/1/26 11/12/25- MCW letter sent to customer 10/15/25- LIRF deemed complete and customer notified 10/2/25- ISD updated to 8/1/26 6/10/25 - per QP meeting ISD moves to 12/31/26. Need a LIRF submitted for this project. 6/2/25- added to potential queue after outreach from ATC asset renewal team reached out about upcoming WPS work at East Krok. | Johanek, Dustin;#107 | MCW
2025-02-28 | 2025-03-17 | 41104 | Wisconsin Public Service | Egg Harbor | Xfmr Repl | 18 | 2026-08-15 | WPS to replace Bank 1 and Bank 2 transformers with new base 12 MVA 69-24.9 kV transformers, upgrade protective relays, and install circuit switchers to the high-side of Bank 1 and Bank 2 transformers. ATC to install new jumpers and insulators to support installation of high-side circuit switchers for Bank 1 and Bank 2 transformers. | 12/2/25 – per QP meeting, ISD moves to 8/15/26 10/2/25 - ISD updated to 09/01/26 6/26/25 - sent PM assigned email, Lynn Kroll 6/4/25- WPS internal engineering assigned this project. Construction will be April - May 2026. 4/16/25 - MCW letter sent to customer on 4/14/25. 3/17/25- LIRF deemed complete and customer notified | Kroll, Lynn;#1170 | MCW
2025-06-09 | 2025-06-23 | 41146 | Wisconsin Public Service | Hilltop | Xfmr Repl | 12 | 2027-11-01 | WPS to replace Bank 1 distribution transformer with 115 kV to 24.94 kV, 22.4 MVA unit. WPS to replace Bank 1 and Bank 2 circuit switchers.ATC to rework the rigid bus as needed to accommodate circuit switcher replacements. | 3/4/26- ISD moves to 11/1/2712/1/25: PM assignment email sent, Bobby Lampshire 7/21/25- MCW letter sent to customer 6/23/25 - LIRF deemed complete, customer notified 3/4/25- added to potential queue per QP discussion. | Lampshire, Robert;#112 | MCW
2023-02-27 | 2023-03-09 | 40341-1 | Wisconsin Public Service | Hodag | Additional Xfmr | 24 | 2026-05-01 | WPS is proposing to install a 2nd 115/24.9 kV, 22 MVA distribution transformer at the Hodag Substation. High-side protection TBD. ATC will consider installing a 138 kV loop through straight bus with provisions for 2 line breakers and a bus-tie breaker. | 10/2/25 - ISD updated to 05/01/26 6/10/25 - per QP meeting, ISD moves to 4/1/26. 12/2/24- per QP meetings, ISD moves to 10/31/25 9/24/24- per QP meeting, ISD moves to 8/31/25 8/5/24- per email from Drew Bain, ISD is pushed out to 12/1/25 on the queue. WPS team is working towards a 8/31/25 ISD with the ATC project team . 8/31/23- PM assigned email sent to customer ​6/1/23- per QP meeting, ISD moves to 6/1/25 ​5/3/23- CW letter executed and returned to ATC ​04/05/23- ICC with CW determination sent to WPS for rev 1 ​3/9/23- LIRF rev 1 deemed complete and customer notified 12/7/22- ISD moves to 12/31/24 per QP meeting 3/9/18- per QP meeting, ISD moves to 2024 09/14/17- Per QP meeting, ISD moves to 6/1/23 09/23/16- moved back to planning queue, ATC planning to begin working on the project 07/18/14- per Planning, move to Inactive queue, project to be reviewed for active status in 2016 06/24/14- LIRF deemed complete and customer notified | Johanek, Dustin;#107 | Alternative Assessment
2025-03-17 | 2025-03-31 | 41116 | Wisconsin Public Service | James Street | High Side Protection Replacement | 18 | 2027-04-01 | WPS to replace the high side protection on the Bank 1 transformer with a new circuit switcher. WPS to upgrade the protective relays, RTU, and feeder exit recloser. ATC to install new jumpers and insulators to support installation of high-side circuit switcher for Bank 1 transformer. | 3/4/26- ISD moves to 4/1/278/15/25 - PM assigned email sent, Bobby Lampshire. 6/4/25- WPS internal engineering assigned this project. Construction will be June 2026. 4/25/25 - MCW letter sent to customer 3/31/25- LIRF deemed complete and customer notified | Lampshire, Robert;#112 | MCW
2025-02-28 | 2025-03-14 | 41103 | Wisconsin Public Service | Sister Bay | Xfmr Repl | 18 | 2027-05-31 | WPS to replace Bank 1 transformer with a new base 12 MVA 69-24.9 kV transformer, upgrade protective relays, and install circuit switchers to the high-side of Bank 1 and Bank 2 transformers. ATC to install new jumpers and insulators to support installation of high-side circuit switchers for Bank 1 and Bank 2 transformers. | 12/2/25 – per QP meeting, ISD moves to 5/31/27 10/2/25- ISD moves to 12/31/27 6/26/25 - sent PM assigned email, Lynn Kroll 6/4/25- WPS internal engineering assigned this project. Construction will be July - August 2026. 4/16/25 - MCW letter sent to customer on 4/14/25. 3/14/25- LIRF deemed complete and customer notified | Kroll, Lynn;#1170 | MCW
2025-02-28 | 2025-03-14 | 41103 | Wisconsin Public Service | Sister Bay | Xfmr Repl | 18 | 2027-05-31 | WPS to replace Bank 1 transformer with a new base 12 MVA 69-24.9 kV transformer, upgrade protective relays, and install circuit switchers to the high-side of Bank 1 and Bank 2 transformers. ATC to install new jumpers and insulators to support installation of high-side circuit switchers for Bank 1 and Bank 2 transformers. | 12/2/25 – per QP meeting, ISD moves to 5/31/27 10/2/25- ISD moves to 12/31/27 6/26/25 - sent PM assigned email, Lynn Kroll 6/4/25- WPS internal engineering assigned this project. Construction will be July - August 2026. 4/16/25 - MCW letter sent to customer on 4/14/25. 3/14/25- LIRF deemed complete and customer notified | Kroll, Lynn;#1170 | MCW
2025-10-16 | 2025-10-30 | 41179 | Wisconsin Public Service | Three Lakes | Xfmr Repl | 12 | 2027-01-31 | WPS to replace existing transformer banks 1 & 2 and feeder arresters (Three Lakes 241 & 242) with new base 12MVA transformers and new station class arresters due to age. WPS to install a portable substation to support the project.ATC to support the connection and disconnection of the WPS portable substation. | 2/17/26 – PM assigned email sent, Erin Cerveny 12/2/25 – per QP meeting, ISD moves to 1/31/27 11/21/25: MCW letter sent 10/30/25 - LIRF deemed complete, customer notified. | Gossen, Erin;#808 | MCW
2025-10-16 | 2025-10-30 | 41179 | Wisconsin Public Service | Three Lakes | Xfmr Repl | 12 | 2027-01-31 | WPS to replace existing transformer banks 1 & 2 and feeder arresters (Three Lakes 241 & 242) with new base 12MVA transformers and new station class arresters due to age. WPS to install a portable substation to support the project.ATC to support the connection and disconnection of the WPS portable substation. | 2/17/26 – PM assigned email sent, Erin Cerveny 12/2/25 – per QP meeting, ISD moves to 1/31/27 11/21/25: MCW letter sent 10/30/25 - LIRF deemed complete, customer notified. | Cerveny, Erin;#808 | MCW
2023-01-25 | 2023-02-08 | 40843 | Wisconsin Rapids Waterworks ＆ Lighting | Northern Casting Steel | Retirement |  | 2024-10-01 | ​WWLC is requesting retirement of the Northern Steel Casting Substation. This facility burnt down about 5 years ago and was never rebuilt. ATC Scope of Work: ATC will investigate what transmission facilities that need to be retired. | 10/24- PM reassigned -Paula Hammersly - Contract PM with oversight from Bobby Lamphsire 2/5/24- ISN received for the tap retirement 1/8/24- ISD moves to 10/1/24 per discussion with regional manager. ​ 8/30/23- PM assigned email sent to customer ​3/6/23- MCW letter sent to customer ​2/8/23- LIRF deemed complete and customer notified | Lampshire, Robert;#112;#Hammersley, Paula;#960 | MCW

## NCW
2026-04-08
ISD has passed
ISD is within 90 days of Queue posting
LIRF/DERRF Received | LIRF/DERRF Complete | LIRF/DERRF ID # | Distribution Customer | Project Name | Project Type | Requested In-Service Date | Projected Scope of Work | Notes & Updates | CPS Coordinator | ATC Commissioning Engineer | ATC System Protection Engineer | BVP Type
2025-01-13 | 2025-01-15 | 41078 | Alliant Energy | 20th St | Sub Rebuild | 2028-12-31 | Due to fault current issues, WPL to replace the aging recloser distribution bay with a 6-feeder switchgear. WPL to retain existing high-side breaker and transformer, retire transformer controls from the ATC control house, and use the standard control package in new switchgear building. | 3/27/26 – Per email updates from Nick H, ISD moves to 12/31/28 2/26/26 – Per QP meeting, ISD moves to 10/1/27 2/12/25- NCW letter sent to customer 01/15/25- LIRF deemed complete and customer notified | Glauser, Chris | Malter, Kevin |  | NCW - LDC Support
2024-07-23 | 2024-08-05 | 41017 | Alliant Energy | Arnott | Sub Rebuild | 2026-09-01 | WPL is replacing their 12kV bus, transformer and high side protection. The site will also be expanded for additional equipment. ATC to install jumpers and insulators to the new high side protective device. ATC to retire existing jumpers and insulators on the box structure. | 2/26/26 – Per QP meeting, ISD moves to 9/1/26 12/9/25- Per QP meeting, contact changes to Greg Shue 10/21/24- NCW letter sent to customer based on discussions with WPL 9/3/24- MCW letter sent to customer 8/5/24- LIRF deemed complete and customer notified |  |  |  | NCW - LDC Only
2025-12-03 | 2025-12-17 | 41198 | Alliant Energy | Artesian | Xfmr Repl | 2028-10-31 | WPL to replace their transformer (T41) at Artesian SS with a new 20 MVA 69-12.47 kV transformer. | 3/27/26 – Per email updates from Nick H, ISD moves to 10/31/28 2/26/26 – Per QP meeting, ISD moves to 12/1/27 2/6/26- NCW letter sent 1/14/26- Initial NCW determination email sent to customer. Letter to follow. 12/17/25 – LIRF deemed complete, customer notified |  |  |  | NCW - LDC Only
2025-05-30 | 2025-06-12 | 41140 | Alliant Energy | Fountain Prairie | Xfmr Repl | 2028-12-31 | WPL to replace distribution transformer at Fountain Prairie with a 138-12.47kV transformer. WPL to replace high side circuit switcher with a 138kV circuit breaker. | 3/27/26 – Per email updates from Nick H, ISD moves to 12/31/28 7/10/25 - NCW letter sent 6/12/25 - LIRF deemed complete, customer notified 12/9/24- added to potential queue per WPL |  |  |  | NCW - LDC Only
2026-01-20 | 2026-02-05 | 41211 | Alliant Energy | Lamar | Xfmr Repl | 2026-06-01 | Alliant Energy (WPL) to replace the 25MVA transformer on Bus 1 with a 50MVA transformer. Alliant Energy (WPL) to install high side breakers for both power transformers | 3/5/26- NCW letter sent 2/5/26- LIRF deemed complete, customer notified |  |  |  | NCW - LDC Only
2023-09-20 | 2023-10-05 | 40897 | Alliant Energy | McFarland (McFarland School) DER | Distributed Energy Resource | 2025-12-01 | Alliant to install 1.4MW of solar DER as part of their customer hosted program. They plan to connect this array to a distribution feeder off bus #1 at the McFarland Substation. No ATC scope of work; all surge arrestors are either upgraded to 106kV MCOV or will be as part of another solar project (17.32MW @ Dane County Landfill – PR08813) at the McFarland substation. | 9/17/25 – Per QP meeting, ISD moves to 12/1/25. 3/6/25- ISD moves to 8/1/25 per QP meeting. 9/27/24- ISD moves to 6/30/25 2/28/24/ - ISD moved to end of December 2024 per feedback from quarterly Planning meeting. 10/26/23- NCW letter and ICC email sent to customer 10/05/23- DERRF deemed complete and customer notified |  |  |  | NCW - LDC Only
2024-09-19 | 2024-09-27 | 41038 | Alliant Energy | Portage | Xfmr Repl | 2028-12-31 | WPL is replacing their existing transformer with a 138/25-12.47kV 33 MVA rated transformer. WPL is replacing the high-side 138 kV circuit switcher with a 138 kV breaker. Connecting to existing insulators. ATC Scope of Work: No Capital Work - LDC Support | 10/29/24- NCW letter and email sent to customer 9/27/24- LIRF deemed complete and customer notified |  |  |  | NCW - LDC Only
2008-11-26 | 2008-12-09 | 40095-1 | Alliant Energy | South Monroe | Sub Rebuild | 2027-12-31 | NCW | 3/27/26 – Per email updates from Nick H, ISD moves to 12/31/27 2/26/26 – Per QP meeting, ISD moves to 8/1/27 6/3/25 - per QP meeting, ISD moves to 3/31/27. 8/16/22- ISD moves to 12/1/26 1/31/22- per update at QP meeting, ISD moves to 12/1/25 9/15/21- ISD moves from 12/1/23 to 12/1/24 3/25/20- per QP meeting, ISD moves to 12/1/23 10/9/19- per QP meeting, ISD is TBD. Moved to 12/1/25 for tracking purposes. 09/11/17- per QP meeting, ISD moves to 12/1/22 12/8/16- per Greg's email, ISD is now 12/1/20 08/08/16- per Greg via email, ISD moves from 12/31/18 to 12/1/19 04/27/16- per QP meeting, ISD moves from 2019 to 2018 02/23/16- per email from Alliant, ISD moves from 6/1/19 to 12/31/19 4/15/14- per QP meeting, ISD moves from 16 to 19 11/12/11 e-mail changing ISD from 15 to 16 | Glauser, Chris |  |  | NCW - LDC Support
2023-01-03 | 2023-01-17 | 40839 | Alliant Energy | Vienna (Walbec Vienna) DER | Distributed Energy Resource | 2025-12-31 | Sunvest will be constructing 1.4 MW of solar DER and transferring ownership to Alliant. Alliant will interconnect the 1.4 MW of solar DER to a Vienna substation feeder (VIEN14817) and may connect to the ATC system through the existing VIE T31 138/12.4 kV, 15/20/25 MVA transformer. ATC scope of work: No Capital Work | 3/6/25- ISD moves to12/31/25 per QP meeting. 12/12/24- revised BVP doc sent to WPL. This is now NCW as the WPL DER at American was placed in-service first. NCW letter sent. 9/27/24-per update at QP meeting, ISD moves to 6/30/25 ​2/7/23- MCW letter and ICC sent to customer ​1/17/23- DERRF deemed complete and customer notified |  |  |  | NCW - LDC Only
2025-02-20 | 2025-03-06 | 41097 | Cloverland Electric Cooperative | Dafter (AlphaWatt) | Load Addition | 2026-12-31 | A third-party customer is adding an additional 3.6 MWs of load as part of a data center facility expansion. The new load will be added at CEC’s Dafter substation. CEC will adjust the existing metering, protection, and voltage regulator settings. CEC will also commission the settings when new load connects. ATC performed local area system impact studies and found no impacts to the transmission system. | 1/26/26- moved to end of the year based on update from Brian L. Some load has been added at the site, but not the full 3.6MW (total would be 7.2MW). 4/21/25- NCW letter sent to customer 3/6/25- LIRF deemed complete and customer notified |  |  |  | TBD
2025-03-18 | 2025-03-27 | 41111 | Consolidated Water Power Company | Rocky Run | High Side Protection Replacement | 2025-08-01 | CWPCo to replace the high-side circuit breaker (#399) and the low-side circuit breaker (5-24S) for Rocky Run transformer T3 with new gas circuit breakers. ATC Scope of Work: No Capital Work (NCW) | 4/25/25: NCW letter and email sent to customer on 4/24/25. There would be ATC support work associated to this project. 3/27/25- LIRF deemed complete and customer notified | Glauser, Chris | Malter, Kevin | Cloninger, Jeff | NCW - LDC Support
2025-04-09 | 2025-04-15 | 41122 | Madison Gas ＆ Electric | Pheasant Branch | Xfmr Repl | 2027-12-31 | MGE to replace the existing transformer at Pheasant Branch with a new 138/69-13.8kV 20/37 MVA distribution transformer. The new transformer will have higher impedance to reduce fault current magnitudes on distribution system. | 11/25/25: per monthly check-in meeting, ISD moves to 12/31/27. 7/14/25 - per QP meeting, ISD moves to 4/1/27. 5/16/25 - NCW work letter sent to customer. 4/16 - LIRF deemed complete 4/14, customer notified 4/15. | Glauser, Chris |  |  | NCW - LDC Support
2025-04-09 | 2025-04-15 | 41121 | Madison Gas ＆ Electric | Sycamore | Xfmr Repl | 2027-12-31 | MGE to replace the existing transformer at Sycamore with a new 138/69-13.8kV 20/37 MVA distribution transformer. The new transformer will have higher impedance to reduce fault current magnitudes on distribution system. | 11/25/25: per monthly check-in meeting, ISD moves to 12/31/27. 10/14/25 – Per QP meeting, ISD moves to 6/1/27 5/16/25 - NCW letter sent to customer. 4/16/25 - LIRF deemed complete 4/14/25, customer notified on 4/15/25. | Glauser, Chris |  |  | NCW - LDC Support
2023-08-04 | 2023-08-18 | 40868-1 | Manitowoc Public Utilities | Custer (MPU Community Garden Solar) | Distributed Energy Resource | 2024-06-01 | Manitowoc Public Utilities installing 1.5 MW of solar DER connected to the Custer T2 (13.8 kV bus). ATC Scope - NCW – LDC only: Custer has 3 network lines, preliminary assessment is no protection or insulation coordination required. | 1/11/24- per update from David England at MPU, ISD moves to 6/1/24 ​8/18/23- DERRF rev1 deemed complete 7/5/23- NCW letter and ICC email sent to customer ​6/7/23- DERRF deemed complete and customer notified |  |  |  | NCW - LDC Only
2025-03-27 | 2025-04-09 | 41119 | Oconto Electric Cooperative | Pioneer Transformer Parelleling | Other | 2025-06-01 | OEC currently operates one of the two 138/34.5kV transformers at Pioneer substation at a time, with the other transformer on standby. OEC to close the high-side switch (299SW) on the Pioneer 138/34.5kV Bank 2 transformer and operate the transformers in parallel. OEC to keep the Bank 2 transformer energized and the low-side load break switch (266LB) will stay a normal open until OEC needs it for loading. | 5/8/25- NCW letter sent to customer 4/9/25- LIRF deemed complete and customer notified |  |  |  | NCW - LDC Only
2025-03-11 | 2025-03-25 | 41109 | Waunakee Utilities | Division Street | High Side Protection Replacement | 2025-12-30 | Waunakee Utilities to upgrade the high side protection on transformer T1 from a fuse to a circuit breaker at Division St substation. At a later date (estimated 2027), Waunakee Utilities to upgrade the Division St transformer to 69-12.49kV 15/28 MVA unit. A new LIRF will be submitted for the transformer replacement. | 4/23/25 - NCW letter sent 3/25/25- LIRF deemed complete and customer notified | Glauser, Chris |  |  | NCW - LDC Support
2025-03-11 | 2025-03-25 | 41110 | Waunakee Utilities | Easy Street (North) | High Side Protection Replacement | 2026-03-01 | Waunakee Utilities to upgrade the high side protection on transformer T1 from a fuse to a circuit breaker at Easy Street substation. ATC Scope of Work: No Capital Work (NCW) | 9/11/25- per 9/11 meeting, ISD moves to 3/1/26. 4/23/25 - NCW letter sent 3/25/25- LIRF deemed complete and customer notified | Glauser, Chris |  |  | NCW - LDC Support
2026-02-19 | 2026-03-05 | 41232 | We Energies | 68th St | Xfmr Repl | 2026-12-31 | WEC to replace 68th St Substation transformers T7 and T8 with 2 new 138-24.94 kV 94.4 MVA units. The scope of work identified in the LIRF does not include any capital work for ATC. | 4/3/26 - update to NCW email - this project is now NCW - ATC support, customer notified 4/3/26 – NCW letter sent 3/5/26- LIRF deemed complete and customer notified | Glauser, Chris |  |  | NCW - LDC Support
2026-02-18 | 2026-03-03 | 41228 | We Energies | Bark River | Xfmr Repl | 2028-03-01 | WEC to replace Bark River T7 with a new 138-24.94 kV 84 MVA transformer. The scope of work identified in the LIRF does not include any capital work for ATC. | 4/3/26 - update to NCW email - this project is now NCW - ATC support, customer notified 4/3/26 – NCW letter sent 3/3/26 – LIRF deemed complete, customer notified | Glauser, Chris |  |  | NCW - LDC Support
2026-02-18 | 2026-03-04 | 41230 | We Energies | Jefferson T7 | Xfmr Repl | 2026-12-31 | WEC to replace Jefferson T7 with a new 138-24.94 kV 84 MVA transformer. The scope of work identified in the LIRF does not include any capital work for ATC. | 4/3/26 - update to NCW email - this project is now NCW - ATC support, customer notified 4/2/26 – NCW letter sent, customer notified 3/4/26- LIRF deemed complete and customer notified | Glauser, Chris |  | Schumann, Douglas | NCW - LDC Support
2026-02-18 | 2026-03-04 | 41231 | We Energies | Jefferson T8 | Xfmr Repl | 2026-12-31 | WEC to replace Jefferson T8 with a new 138-24.94 kV 84 MVA transformer. The scope of work identified in the LIRF does not include any capital work for ATC. | 4/3/26 - update to NCW email - this project is now NCW - ATC support, customer notified 4/2/26 – NCW letter sent, customer notified 3/4/26- LIRF deemed complete and customer notified | Glauser, Chris |  | Schumann, Douglas | NCW - LDC Support
2026-02-19 | 2026-03-06 | 41233 | We Energies | Moorland T8 | Xfmr Repl | 2026-12-31 | WEC to replace Moorland Substation transformer T8 with a new 138-24.94 kV 91.1 MVA unit. | 4/6/26 – NCW letter sent, this project is now NCW - ATC support, customer notified 3/6/26- LIRF deemed complete, customer notified | Glauser, Chris |  |  | NCW - LDC Support
2022-07-01 | 2022-07-15 | 40798 | We Energies | Root River | Xfmr Repl | 2026-02-15 | ​WEC to replace both distribution transformers (T7 and T8) with new 138/24.9 kV, 42/56/70 MVA units. ATC Scope: No breakers need, likely NCW – LDC Only. | 09/25/25- ISD moves to 2/15/26 3/5/25- per QP meeting, ISD moves to 2/1/26 12/4/24- ISD moves up to 12/31/26 3/12/24 - WE notified that replacement is no longer part of 2025 work plan, likely out a few years. New tentative ISD is 12/1/27. ​8/10/22- NCW letter sent to customer 7/15/22- LIRF deemed complete and customer notified |  |  |  | NCW - LDC Only
2023-02-27 | 2023-03-13 | 40850 | We Energies | St Rita Cap Bank Removal | Retirement | 2026-05-01 | ​WEC is requesting to retire the St. Rita distribution cap bank. ATC to determine if a system study is needed. NCW, if retirement has no transmission system impacts | 5/29/25 - per QP meeting, ISD moves to 5/1/26. 3/13/24- ISD updated to 6/1/25 at QP meeting ​06/08/23- per QP meeting, ISD moves to 4/30/24 ​4/10/23- NCW and ICC email sent to customer ​3/13/23- LIRF deemed complete and customer notified |  |  |  | NCW - LDC Only
2025-03-04 | 2025-03-17 | 41105 | Wisconsin Public Service | Highway 8 | Xfmr Repl | 2027-11-01 | WPS to replace Bank 1 & Bank 2 transformers with new base 12 MVA 115/24.9 kV transformers. WPS to upgrade Feeder 243 protective relay & feeder exit breaker. | 3/4/26- ISD moves to 11/1/27 10/2/25 - ISD updated to 6/30/27 4/16/25 - NCW letter sent to customer on 4/14/25. 3/17/25- LIRF deemed complete and customer notified ​1/25/23- Added to potential queue via email from Steve Herbel | Glauser, Chris | Malter, Kevin |  | NCW - LDC Support
2023-05-31 | 2023-06-13 | 40869 | Wisconsin Public Service | Pearl Ave | Xfmr Repl | 2028-12-01 | WPS will replace the Bank 1 and 2 transformers with 69/24.9 kV, 15 MVA base transformer. Existing high side switches/protection to be retained. No ATC capital work anticipated. Verified no high-side work to be completed with WPS. | ​​​8/23/23- per update from Logan P, ISD moves to 12/1/28 ​07/11/23- NCW letter and ICC sent to customer ​06/13/23- LIRF deemed complete and customer notified 6/9/22- ISD moves to 12/1/26 per QP meeting 2/26/20- added to potential queue per QP meeting |  |  |  | NCW - LDC Only
2025-06-09 | 2025-06-23 | 41145 | Wisconsin Public Service | Summit Lake | Xfmr Repl | 2026-12-31 | WPS to replace Bank 1 and 2 transformers with 22.4 MVA units.WPS to upgrade substation fencing with High Security fence. | 7/21/25- NCW letter sent to customer 6/23/25 - LIRF deemed complete and customer notified. |  |  |  | NCW - LDC Only

## In-active
2026-04-08
ISD has passed
ISD is within 90 days of Queue posting
LIRF/DERRF Received | LIRF/DERRF Complete | LIRF/DERRF ID # | Distribution Customer | Project Name | Project Type | Estimated ATC Project Lead-Time After PCA Execution | Requested In-Service Date | Projected Scope of Work | Notes & Updates | ATC Planner | BVP Type
2019-08-14 | 2019-08-28 | 40578 | Alliant Energy | Bonnie Road | New Sub | 24 | 2028-12-31 | WPL to construct a new Drumlin Substation with one 69/12 kV, 33 MVA transformer. ATC to extend 0.5 mile of 69 kV radial tap off line Y-81 (Sun Prairie – Kegonsa). | 2/26/26 – Per QP meeting, looking for new property location 6/2/25 - per QP meeting, project on hold pending real estate issues. WPL to submit revised LIRF when ready. 3/6/25- ISD moves to 2028 per QP meeting. 9/27/24- per planning meeting, ISD moves to 12/31/27. WPL to submit revised LIRF. 8/20/24- moved back into planning. Discuss with WPL, is a revised LIRF needed? 2/28/24- per QP discussion, ISD moves to 12/31/26 ​4/5/23- ISD moves to 12/31/25 1/31/22- per Greg A, ISD moves to 12/31/24 7/23/21- PM assigned, customer notified 3/22/21- CW letter executed 3/9/21- per QP meeting, name is updated to Bonnie Road 8/28/19- LIRF deemed complete and customer notified | Mainwaring, Kyle | Alternative Assessment
2024-07-23 | 2024-08-05 | 41016 | Alliant Energy | Friendship | Sub Rebuild | 18 | 2028-12-31 | Alliant is planning to relocate their Friendship sub away from the nearby lake due to access issues. They have been working on securing new land, but have not been able to finalize a new location for the substation at this point. ATC scope will be dependent on the new sub location. Ryan informed ATC planning that he will stay in communication regarding the land acquisition progress. | 2/26/26 – Per QP meeting, looking for new property location 6/3/25 - per QP meeting, ISD moves to 2028. dependent on land purchase. 5/9/25 - placing project 'on hold' per WPL. 9/3/24- ICC email sent to customer, ATC scope TBD until location is selected 8/5/24- LIRF deemed complete and customer notified 8/16/22- ISD moves to 6/1/26 1/31/22- per QP meeting, ISD moves to 6/1/25 6/15/21- Added per QP Meeting | Mainwaring, Kyle | Alternative Assessment
2024-07-26 | 2024-08-08 | 41019 | Alliant Energy | Huebner | 3rd Xfmr | 24 | 2027-12-31 | Alliant is planning to add a third transformer to the Huebner substation, with an open-air bus or switchgear design depending on available space. ATC Scope of Work: Relocate cap bank and breaker on the west side of the station. Add bus supports and connection to new Alliant transformer. Install 1 bus tie breaker and 2 line breakers. | 11/14/24- per update from Alliant, this project is on hold as Alliant looks at the surrounding area, Alliant’s long-term needs and what other projects they might identify. 9/12/24- ICC email with capital work determination sent to customer. CW letter to follow at later date. 8/8/24- LIRF deemed complete and customer notified | Mainwaring, Kyle | Alternative Assessment
2013-12-04 | 2013-12-13 | 40317 | Alliant Energy | Rosholt | Xfmr Repl | 18 | 2027-06-01 | Install temporary facilities at Rosholt Substation to accommodate the transformer replacement | 12/9/25- Per QP meeting, contact changes to Greg Shue 09/11/17- per QP meeting, ISD moves to 6/1/27 04/4/17- per QP meeting, move to on hold queue. Sub is likely to retire 04/27/16- per QP meeting, ISD moves from 5/1/16 to 5/1/18 01/30/15- per new Alliant schedule, ISD moves from 5/1/15 to 5/1/16 4/7/14- per RM, PCA will not be needed, will most likely by MCW. Customer notified of PM assignment. 3/31/14- PR is approved and PM has been assigned 3/14/14- Per M.Waldron, PR is submitted and awaiting PM assignment 1/21/14- Alliant to determine if mobile SS is needed, if mobile SS is needed project will be NCW; waiting for reply from Alliant 12/17/13 ATC informed Alliant that LIRF rev. 0 is complete | Brecklin, Logan | MCW
2016-08-22 | 2016-08-25 | 40229-1 | Upper Peninsula Power Company | Chatham | Xfmr Repl | 24 | 2026-12-31 | change to Bk1 Transformer Replacem | 10/2/24- on hold per update from UPPCO at QP meeting. 10/5/22- per QP meeting, ISD moves to 12/31/26 5/9/22 Per QP meeting scope updated 2/1/21- per UPPCO, ISD moves to 12/31/24 4/15/20 - per QP meeting, ISD moves to 12/31/23 9/24/19- Per UPPCO capital plan, ISD moves to 12/31/22 4/15/19- per QP meeting, ISD moves to 6/1/22 10/20/17- per QP meeting, ISD moves to 2021 4/4/17- per QP meeting, ISD is 6/1/19 08/25/16- LIRF revision deemed complete and customer notified 07/10/13 per UPPCO, on hold 01/05/12 informed UPPCo LIRF is complete | Pirkola, Logan | Alternative Assessment
2020-04-16 | 2020-04-27 | 40624 | Upper Peninsula Power Company | Keweenaw | Other Substation Equipment Modification | 6 | 2025-12-31 | UPPCO to replace existing 69-kV fuse with circuit switcher or circuit breaker. ATC to provide protection and commissioning support. High-side disconnect switch will remain the same. | 5/8/25 - per QP meeting, moving this project to 'on hold'. 10/2/24- per QP meeting, ISD moves to 12/31/25 5/7/24 - Update from quarterly planning meeting is that his work has moved up to end of 2025, changed ISD to 11/14/25 5/9/22 Per QP meeting ISD updated 10/26/21- ISD moves from 2022 to 2025, per UPPCO QP meeting 4/22/21- NCW letter sent to customer 4/27/20- LIRF deemed complete and customer notified. Previous LIRF #40501 has been cancelled. | Brecklin, Logan | NCW - LDC Support
2020-10-15 | 2020-10-23 | 40224-2 | Upper Peninsula Power Company | M-38 | Additional Xfmr | 42 | 2025-10-15 | UPPCO to add a 138/12.47 kV, 7 MVA unit. UPPCO to utilize 138 kV 2619A bus switch as interconnection point. Fuse as high-side protection. Secondary to be fed underground to spare 12 kV feeder position, and UPPCo to replace 745 recloser with circuit breaker. | 5/8/25 - per QP meeting, put project on hold due to equipment availability. ISD will be changing, indication of no sooner than 2026. 12/14/23- ISD updated to 10/15/2025 via email from Dan Gervae. Shared with Adam Brecklin (CPS coordinator). ​4/19/23- NCW letter sent to customer 10/21/22- update provided by UPPCO, ISD is 12/1/25. ATC will need to cancel current PR and submit new PR for expanded scope. 5/9/22 Per QP meeting ISD updated 11/16/20- initial customer communication sent to customer 10/23/20- LIRF rev 2 deemed complete and customer notified 4/15/20- per QP meeting, ISD moves to 12/1/24 2/20/20- per email with Tim, ISD is 12/1/25 5/2/19- per UPPCO Capital Plan, ISD is TBD 4/15/19- per QP meeting, ISD moves to 10/1/22 2/25/19- PM assigned and customer notified 2/20/19- CW letter executed and saved to IRM 10/20/17- per QP and UPPCO capital plan, ISD moves to 2020. 03/30/17- LIRF revision deemed complete and customer notified 10/14/16- per UPPCO Capital Plan, ISD moves to 2020 07/10/13 per UPPCO, on hold 12/22/11 informed UPPCO that LIRF is Complete: on Potential queue because of the 2019 ISD; Construction Lead Time: 2 years, Planning Lead time: 6 months, Start Date: June 2016 | Brecklin, Logan | NCW - LDC Support

## Definitions
Queue Column Heading | Definition
Action Items | What may be needed for the LIRF/DERRF to be deemed complete, the BVP process to commence or complete, the PCA process to commence or complete, or involve construction of the project. It is meant to denote what is needed for the project to move forward.
Agreement Sent Date | Date a final PCA is sent to the Customer for signature. Enter “N/A” if a PCA is not required (esp. for legacy projects) and for No Capital Work projects.
Agreement Signed Date | Date the PCA is signed by the last party. For Network Projects this would be the date our customer signs the agreement, for regular and end use projects it would be the date ATC signs the agreement. Enter “N/A” if a PCA is not required (esp. for legacy projects) and for No Capital Work projects.
ATC Planner | ATC planner responsible for the project.
BVP (Best Value Plan) Levels | No Capital Work (LDC Only or LDC Support) - No ATC Capital Work and no transmission analysis
Minimal Capital Work - Minor amount of ATC infrastructure to be installed. Minimal ATC Capital Work and no transmission analysis
Alternative Assessment - May include a transmission alternatives for interconnecting the load to the transmission system or assessment of multiple substation configurations. Potential for planning analysis of alternatives including a difference analysis (compared to the base case model) and possibly different transmission system network and load configurations – amount determined by engineering judgment and team meetings
System Study - Transmission Analysis - Modeling analysis for at least two alternatives including a difference analysis (compared to the base case model) including NERC TPL contingencies with different transmission system network and load configurations. Modeling will encompass at least a 10 year planning horizon
System Study and PSCW Filing - ATC needs to file a Certificate of Authority (CA) or Certificate of Public Convenience and Necessity (CPCN) with the PSCW
CPCN Requirements: > 1 mile of new ROW, ≥115 kV; 30 months lead time for CPCN process, 54 months total project
Distribution Customer | The Company that submitted the LIRF or DERRF.
Distribution Customer Contact | Customer contact for the project.
E.D. = Economic Development | Mark Y or N to tell if the project is due un-forecasted load or not
Estimated ATC Project Lead-Time after PCA Execution | The amount of time (in months) that ATC requires to complete its Projected Scope of Work after receiving a customer signed PCA. In the earliest stages of project planning and until ATC can define any specific scope for work, the following default leadtimes will apply based upon Project Type: New Substation: 54 months Load Addition, Loop thru bus, Loop thru bus w/ breaker, Substation Rebuild, Additional Transformer, Other: 24 months Retirement, Distribution Connected Generation, Replacement Transformer: 18 months No Capital Work: 0 months
LIRF/DERRF Complete | The date that ATC deemed the LIRF or DERRF complete.
LIRF/DERRF ID No. | Sequential number given to each submitted LIRF or DERRF. (5 digit number - revision number, example 40000-1)
LIRF/DERRF Received | The date the Customer submitted a Load Interconnection Request Form (LIRF) or DER Request Form (DERRF) to ATC. An email notification is sent to the customer once the LIRF/DERRF has been deemed complete by ATC's Planning department.
Notes & Updates | Anything that is essential to properly considering the project schedule and/or progress. Can be used in facilitating meetings with the customer.
Notification Type | How ATC was notified of the project. Examples include, Quarterly Planning Meetings, public announcements, project meetings… (Potential Projects).
PCA No. | The number assigned to a Project Commitment Agreement (PCA) between ATC and the customer. The number (XXXX-X) represents the year the agreement was signed in followed by a dash and the total number of agreement signed up to the date of the new agreement. If an amendment to a PCA occurs the number length will extend to XXXX-X-X. All numbers are assigned by ATC's Interconnection Services Administrator.
PR No. | The identification number assigned to an approved project request (PRF). This process allocates dollars to the project.
Project Manager | ATC’s project manager responsible for implementing ATC’s engineering and construction portion of the project after a PRF is approved. Responsible for the development and execution of a Project Commitment Agreement (PCA), if one is necessary.
Project Name | As represented by the Customer on the LIRF, the name of the substation (new or existing) at which the load interconnection addition or change will take place.
Project Notification Date | The date ATC was notified of a potential project. (Potential Projects).
Project Type | General descriptions summarizing the Customer's scope of work.
Projected Scope of Work | A description of ATC's scope of work as best known at any given point in the development or implementation of the project. It should include a summary of key configuration elements and any related network reinforcements.
Requested In-Service Date | The in-service date most recently approved by the customer as representing their present needs. "TBD" indicates a date has not yet been determined.