## ReadMe
ATC Area Generator Material Modification (MM) Study Review Template -V0 |  | Revision History
|  | Revision | Date | Summary of Changes
|  | V0 | 2023-03-13 | Initial Document
Instructions for Generator Interconnection Customers
1 | The generator MM study review template should be used when an Interconnection Customer (IC) in ATC area plans to submit a generator MM study to MISO prior to commercial operation. Please refer to MISO’s Tariff Attachment X Section 4.4 for more information on Generator Modification (GM) Process.
2 | The purpose of this document is two-fold. (1) It provides ICs a list of information required by ATC to review/approve a generator MM study prior to commercial operation. (2) Using this template, it would allow ATC to conduct a thorough review of the generator MM study in a more efficient way and minimize potential delays.
3 | If applicable, an IC should provide all the information requested on the following tabs of the spreadsheet.
- "GM Description" tab
- "GM Plant Data" tab
- "GM Short Circuit Data" tab
- "MM Steady State Analysis" tab
- "MM Power Factor Analysis" tab
- "MM Stability Analysis" tab
4 | Additional required documents are listed on the "Required Documents" tab and should be provided together with this spreadsheet to MISO when submitting a generator MM study prior to commercial operation.
5 | ICs do not need to provide a short circuit study. ATC Protection needs to re-evaluate the short circuit impact of the generator modification request based on the GM short circuit data.
6 | For questions related to the generator MM study review template, please send them to Chengyue Guo (cguo@atcllc.com) and Damien Sommer (dsommer@atcllc.com) in ATC Resource Interconnections team.

## Required Documents
The following documents should be provided when an IC in ATC area submits a generator MM study to MISO prior to commercial operation.
Document ID | Description ( Information should match the generator modification request) | Provided ? (Yes or No or N/A)
1 | This spreadsheet with requested information filled out
2 | IC Oneline
3 | PSSE .raw file for the standalone plant (V34 or higher)
4 | PSSE slider diagram for the standalone plant (V34 or higher)
5 | PSSE idev for the standalone plant (V34 or higher)
6 | P-Q Curve
7 | Test reports for generator step-up transformer and main power transformers if available
8 | ENTIRE ERIS and NRIS steady-state study package ( i.e. models, input and output files)
9 | PSSE dyre file
10 | ENTIRE TSAT study package (i.e., all *.tsa, *.pfb, *.dyr, *.mon, *.dat, GNET, etc.) and all the output files (i.e., all *.olf, *.bin, *.prg, etc.)
11 | PSCAD model and documentation for inverter-based resource
12 | PSCAD model verification document for inverter-based resource (see Note 1 below)
13 | Updated PSCAD study report if a PSCAD study was performed in MISO DPP system impact study (See Note 2 below)
Notes
1 | ATC Inverter-Based Resource (IBR) PSCAD Model Verification related documents can be downloaded from the link below. The checklist must be completed to show that the PSCAD plant model meets all ATC PSCAD modeling requirements for ATC to accept the PSCAD plant model
https://www.atcllc.com/customer-engagement/connecting-to-the-grid
2 | An IC needs to make a study deposit to MISO for the MM PSCAD study. MISO will contract ATC to perform the MM PSCAD study.
3 | An IC can provide other documents if they are helpful to the MM review process.
Note on C3: ATC: Please fill out this column before submitting.

## GM Description
Questions | Answers
Does the generator modification request change the original Point of Interconnection (POI)? | Yes
If the answer is Yes, please provide the new POI coordinates (longitude, latitude) in a decimal degree format (please do not use a degree/minute/second format) | -88.15267 43.129308
Please provide a general description about the generator modification request below.
Note on B2: ATC: These are sample answers. Please update to match the MM request.

## GM Plant Data
Generator Modification Plant 1 Data |  |  | Generator Modification Plant 2 Data (if applicable) |  |  | Generator Modification Plant 3 Data (if applicable) |  |  | Generator Modification Plant 4 Data (if applicable)
Equipment | Parameter | Value(s) | Equipment | Parameter | Value(s) | Equipment | Parameter | Value(s) | Equipment | Parameter | Value(s)
Generator 1 | Generator Voltage kV | 0.63 | Generator 2 | Generator Voltage kV |  | Generator 3 | Generator Voltage kV |  | Generator 4 | Generator Voltage kV
| Generator MVA Mbase | 58.8 |  | Generator MVA Mbase |  |  | Generator MVA Mbase |  |  | Generator MVA Mbase
| Generator MW capability | 52.92 |  | Generator MW capability |  |  | Generator MW capability |  |  | Generator MW capability
| Generator MVAR capability | +25.63/-25.63 |  | Generator MVAR capability |  |  | Generator MVAR capability |  |  | Generator MVAR capability
| Generator PF (lag/lead) | 0.87 lag / 0.94 lead |  | Generator PF (lag/lead) |  |  | Generator PF (lag/lead) |  |  | Generator PF (lag/lead)
| Generator scheduled voltage in per unit | 1.02 |  | Generator scheduled voltage in per unit |  |  | Generator scheduled voltage in per unit |  |  | Generator scheduled voltage in per unit
| Remote Bus Number (POI bus) for scheduled voltage | 999901 |  | Remote Bus Number (POI bus) for scheduled voltage |  |  | Remote Bus Number (POI bus) for scheduled voltage |  |  | Remote Bus Number (POI bus) for scheduled voltage
| # of inverters that make up the generator | 14 |  | # of inverters that make up the generator |  |  | # of inverters that make up the generator |  |  | # of inverters that make up the generator
| Individual inverter MVA capability | 4.2 |  | Individual inverter MVA capability |  |  | Individual inverter MVA capability |  |  | Individual inverter MVA capability
| Individual inverter MW capability | 3.78 |  | Individual inverter MW capability |  |  | Individual inverter MW capability |  |  | Individual inverter MW capability
| Inverter Type/Make | SolarKing G1234 |  | Inverter Type/Make |  |  | Inverter Type/Make |  |  | Inverter Type/Make
| Fuel Type | Solar |  | Fuel Type |  |  | Fuel Type |  |  | Fuel Type
| Rs, Xs | 0, 9999 |  | Rs, Xs |  |  | Rs, Xs |  |  | Rs, Xs
GSU 1 | GSU Low voltage winding kV | 0.63 | GSU 2 | GSU Low voltage winding kV |  | GSU 3 | GSU Low voltage winding kV |  | GSU 4 | GSU Low voltage winding kV
| GSU Low voltage winding configuration | Y |  | GSU Low voltage winding configuration |  |  | GSU Low voltage winding configuration |  |  | GSU Low voltage winding configuration
| GSU High voltage winding kV | 34.5 |  | GSU High voltage winding kV |  |  | GSU High voltage winding kV |  |  | GSU High voltage winding kV
| GSU High voltage winding configuration | Delta |  | GSU High voltage winding configuration |  |  | GSU High voltage winding configuration |  |  | GSU High voltage winding configuration
| GSU No Load Tap settings | 5 taps, +/- 5% |  | GSU DETC settings |  |  | GSU DETC settings |  |  | GSU DETC settings
| GSU No Load Tap setting kV | 34.5 |  | GSU No Load Tap setting kV |  |  | GSU No Load Tap setting kV |  |  | GSU No Load Tap setting kV
| # of Padmount transformers that make up the GSU | 14 |  | # of Padmount transformers that make up the GSU |  |  | # of Padmount transformers that make up the GSU |  |  | # of Padmount transformers that make up the GSU
| Individual padmount transformer MVA rating | 4.2 |  | Individual padmount transformer MVA rating |  |  | Individual padmount transformer MVA rating |  |  | Individual padmount transformer MVA rating
| %Z1 and the Mbase it is on | 5.75% , 4.2 MVA |  | %Z1 and the Mbase it is on |  |  | %Z1 and the Mbase it is on |  |  | %Z1 and the Mbase it is on
| X/R ratio assumption | 7.5 |  | X/R ratio assumption |  |  | X/R ratio assumption |  |  | X/R ratio assumption
Collector System 1 | Per unit impedance R,X & B value (not B/2) | 0.000737, 0.000756, 0.008262 | Collector System 2 | Per unit impedance R,X & B value (not B/2) |  | Collector System 3 | Per unit impedance R,X & B value (not B/2) |  | Collector System 4 | Per unit impedance R,X & B value (not B/2)
| Equivalent collector system facility rating in MVA | 117.6 |  | Equivalent collector system facility rating |  |  | Equivalent collector system facility rating |  |  | Equivalent collector system facility rating
MPT 1 | MPT Low voltage winding kV | 34.5 | MPT 2 | MPT Low voltage winding kV |  | MPT 3 | MPT Low voltage winding kV |  | MPT 4 | MPT Low voltage winding kV
| MPT Low voltage winding configuration | YG |  | MPT Low voltage winding configuration |  |  | MPT Low voltage winding configuration |  |  | MPT Low voltage winding configuration
| MPT High voltage winding kV | 69 |  | MPT High voltage winding kV |  |  | MPT High voltage winding kV |  |  | MPT High voltage winding kV
| MPT High voltage winding configuration | YG |  | MPT High voltage winding configuration |  |  | MPT High voltage winding configuration |  |  | MPT High voltage winding configuration
| MPT No Load Tap settings | 5 steps, +/- 5% |  | MPT No Load Tap settings |  |  | MPT No Load Tap settings |  |  | MPT No Load Tap settings
| MPT No Load Tap setting kV | 69 |  | MPT No Load Tap setting kV |  |  | MPT No Load Tap setting kV |  |  | MPT No Load Tap setting kV
| Transformer MVA ratings (i.e. 75/100/125) | 40/50/65 |  | Transformer MVA ratings (i.e. 75/100/125) |  |  | Transformer MVA ratings (i.e. 75/100/125) |  |  | Transformer MVA ratings (i.e. 75/100/125)
| %Z1 and the Mbase it is on | 9% , 40 MVA |  | %Z1 and the Mbase it is on |  |  | %Z1 and the Mbase it is on |  |  | %Z1 and the Mbase it is on
| X/R ratio assumption | 40 |  | X/R ratio assumption |  |  | X/R ratio assumption |  |  | X/R ratio assumption
| If equipped with a LTC, what are the settings and on which side | 33 taps, +/- 10 % on 69 kV side |  | If equipped with a LTC, what are the settings and on which side |  |  | If equipped with a LTC, what are the settings and on which side |  |  | If equipped with a LTC, what are the settings and on which side
Gen Lead Line 1 | Per unit impedance R,X & B value (not B/2) | 0.00104, 0.00502, 0.00011 | Gen Lead Line 2 | Per unit impedance R,X & B value (not B/2) |  | Gen Lead Line 3 | Per unit impedance R,X & B value (not B/2) |  | Gen Lead Line 4 | Per unit impedance R,X & B value (not B/2)
| Line rating in MVA (PSSE RATE 1) | 185 |  | Line rating (Rate 1) |  |  | Line rating (Rate 1) |  |  | Line rating (Rate 1)
| Line length (Miles) | 0.35 |  | Line length |  |  | Line length |  |  | Line length
| Line conductor | N/A |  | Line conductor |  |  | Line conductor |  |  | Line conductor
Plant Cap Banks 1 | # of banks, MVAR per bank | 2 , 4 Mvar | Plant Cap Banks 2 | # of banks x MVAR per bank |  | Plant Cap Banks 3 | # of banks x MVAR per bank |  | Plant Cap Banks 4 | # of banks x MVAR per bank
| Voltage kV | 34.5 |  | Voltage kV |  |  | Voltage kV |  |  | Voltage kV
Note on C2: ATC: These are sample values. Please update to match the MM request.
Note on C8: ATC: This is an ATC Planning Criteria Requirement. Please make sure the voltage schedule is included in all study models with the remote controlled bus set as the POI bus.
Note on K8: ATC: This is ATC Planning Criteria Requirement. Please make sure the voltage schedule is included in all study models with the remote controlled bus being the POI bus.
Note on O8: ATC: This is ATC Planning Criteria Requirement. Please make sure the voltage schedule is included in all study models with the remote controlled bus being the POI bus.
Note on S8: ATC: This is ATC Planning Criteria Requirement. Please make sure the voltage schedule is included in all study models with the remote controlled bus being the POI bus.
Note on A31: ATC: Three winding transformers add a node not assigned to a PSSE bus number which must be initialized for every model build. Past experience has shown that these nodes not assigned to a PSSE bus number have been a source for power flow model solution difficulties. Since the third winding, when it has no devices such as a shunt or load connected to it, has no impact on the steady-state modeling ATC has opted to not model them. The three-winding transformers will be modeled as a three-winding transformer for the short circuit study. See the "MM Short Circuit Data" tab.

## GM Short Circuit Data
If applicable, please provide the short circuit generator modeling data for the generator modification request (inverter-based resources).
Notes: 1. For multiple generators or transformers, please add additional rows under the tables. 2. ICs do not need to provide a short circuit study. ATC Protection needs to re-evaluate the short circuit study to determine the impact of the generator modification based on the information below.
Generator Data
Fuel Type | Terminal Voltage (KV) | Aggregate MW | Aggregate MVA | Data Required for Inverter-Based Resources
|  |  |  | Inverter Type (Type 3 - Doubly-Fed Induction OR Type 4 - Full Converter) | Inverter Model | Total # of Inverters | Individual Inverter Rated MVA | Individual Inverter Rated Power Factor | Inverter Short Circuit Contribution (P.U. Subtransient Current Limit - 2-3 cycles after fault)
Generator Setup Transformer (GSU) Data
Voltage (High/Low) kV | Total # of Pad Mount Transformer | Winding | %Z1 | X/R | MVA Base for Impedance Calc
H-X
Main Power Transformer (MPT) Data
Voltage (High/Low/Tertiary) kV | Winding Connection (High /Low /Tertiary) | Winding | %Z1 | %Z0 | MVA Base for Impedance Calc
H-X
H-T
X-T
Note: Positive Sequence Impedance data for H-T and X-T are not required. But if available, please provide.
Gen-Tie Line Impedance Data
Line kV | MVA Base for Impedance Calc | R1 (pu) | X1 (pu) | B1 (pu) | R0 (pu) | X0 (pu) | B0 (pu)
Note: Zero Sequence Impedance data for Gen-Tie are not required. But if available, please provide.
Note on B17: Guo, Chengyue: Please note: ATC requires that this transformer have a high-side ground connection and a delta-connected winding; examples of acceptable connections include wye-ground/delta two winding transformer, wye-ground/delta/wye-ground three winding transformer, and autotransformer with a delta tertiary winding.

## MM Steady State Analysis
If applicable, please provide a description of the MM steady-state analysis (ERIS and/or NRIS), the MM study conclusion and the MM study summary result tables below to support the conclusion.
Notes: 1. For the steady-state analysis, please use the final ERIS or NRIS steady-state study package from the MISO DPP that is applicable for the generator modification request.

## MM Power Factor Analysis
If applicable, please fill out the power factor study tables below for the generator modification request and provide PSSE slider diagrams that match the data in Table 2 and Table 3 (examples provided).
Notes: 1. Blue font data in the tables are sample values as an example. Please update with the power factor study data for the generator modification request. 2. Red font data in the tables are based on built-in formulas. Please do not change. 3. For multiple generators, please add additional rows under the tables as needed.
Table 1 - MM Plant Reactive Resources
MISO Queue # | Machines |  |  |  | Dynamic Devices |  |  | Static Devices
| Fuel Type | Real Power (MW) | Capacitive Reactive Power (MVAR) | Inductive Reactive Power (MVAR) | Description | Capacitive Reactive Power (MVAR) | Inductive Reactive Power (MVAR) | Description | Capacitive Reactive Power (MVAR) | Inductive Reactive Power (MVAR)
Jxxxx | Solar | 227.92 | 116.767 | -116.767 | None | N/A | N/A | 2 X 4 MVAR | 8 | 0
Table 2 - MM Capacitive Power Factor Evaluation @ Pmax/Qmax with the infinite machine to control voltage on the bus where PF is to be calculated to 0.95 p.u.
MISO Queue # | Machine Terminal Bus # | MW at Machine Terminal | MVAR at Machine Terminal | Additional Dynamic MVARs provided by Interconnection Request | Dynamic Power Factor Provided | Meets 0.95 ATC Capacitive Dynamic Power Factor Requirement? | Additional Dynamic MVARs required to meet ATC Capacitive Power Factor Requirement
Jxxxx | 999901 | 227.92 | 116.767 | 0 | 0.89 | Yes | 0
MISO Queue # | POI Bus Number (synchronous) or HV Bus (asynchronous) | MW at POI (synchronous) or HV Bus (asynchronous) | MVAR at POI (synchronous) or HV Bus (asynchronous) | POI (synchronous) or HV Bus (asynchronous) Power Factor | Meets 0.95 ATC Capacitive Power Factor Requirement at POI Bus (synchronous) or HV Bus (asynchronous)? | Additional Static MVARs required at POI Bus (synchronous) or HV Bus (asynchronous) to meet ATC Capacitive Power Factor Requirement
Jxxxx | 999902 | 223 | 72.6 | 0.95 | Yes | 0
Table 3 - MM Inductive Power Factor Evaluation @ Pmax/Qmin with the infinite machine to control voltage on the bus where PF is to be calculated to 1.05 p.u.
MISO Queue # | Machine Bus | MW at Machine Terminal | MVAR at Machine Terminal | Additional Dynamic MVARs provided by Interconnection Request | Dynamic Power Factor Provided | Meets 0.95 ATC Inductive Dynamic Power Factor Requirement? | Additional Dynamic MVARs required to meet ATC Capacitive Power Factor Requirement
Jxxxx | 999901 | 227.92 | 116.767 | 0 | 0.89 | Yes | 0
MISO Queue # | POI Bus (synchronous) or HV Bus (asynchronous) | MW at POI (synchronous) or HV Bus (asynchronous) | MVAR at POI (synchronous) or HV Bus (asynchronous) | POI (synchronous) or HV Bus (asynchronous) Power Factor | Meets 0.95 ATC Inductive Power Factor Requirement at POI Bus (synchronous) or HV Bus (asynchronous)? | Additional Static MVARs required at POI Bus (synchronous) or HV Bus (asynchronous) to meet ATC Capacitive Power Factor Requirement
Jxxxx | 999902 | 223 | 72.6 | 0.95 | Yes | 0
Table 4 - MM Assessment of Reactive Power Injection to the Transmission System When Non-synchronous Generator is at zero MW output
MISO Queue # | Per ATC Planning Criteria, when non-synchronous Generating Facility is not generating active power (i.e. zero MW output), the reactive power injection to the transmission system at the high-side of the generator substation should be zero Mvar. Can the MM plant meet this requirement? and How? | [5 empty] | If the answer is Yes, please describe how the requirement would be met.
Jxxxx | Yes

## MM Stability Analysis
If applicable, please provide a description of the MM stability analysis for the generator modification request and the conclusion on this tab.
Notes: 1. For the stability analysis, please use the final stability package from the MISO DPP that is applicable for the generator modification request. 2. Interconnection Customer needs to run the MISO DPP fault file (TSAT .swi file) developed for the specific study generator. 3. At a minimum, the following channel files should be created for all machines at the same POI. - machine angle - machine terminal voltage - machine active power output - machine reactive power output - POI bus voltage 4. Applicable ATC Planning Criteria (dynamic stability criteria including IBR stability criteria) can be located in Appendix B of the applicable DPP System Impact Study Report. 5. Per ATC Planning Criteria, any generator interconnected within the ATC system is expected to maintain a voltage schedule (voltage setpoint) of 1.02 p.u. at its POI, within limits of its reactive capabilities,