## Read Me
ATC PSCAD Plant Model Verification Checklist -V2 |  | Revision History
The purpose of this checklist is to aid Interconnection Customers/Generator Owners in submitting PSCAD plant models that meet ATC Planning Criteria. |  | Revision | Date | Summary of Changes
|  | 1 | 2023-03-29 | New Document
Instructions for Generator Interconnection Customers/Generator Owners |  | 2 | 2024-02-23 | New Document
1 | This checklist should be completed and sent to ATC with every PSCAD plant model submission.
2 | The Interconnection Customer/Generator Owner should input comments for every item on the following tabs:
Usability
PSSE-PSCAD Data Comparison
Tests
3 | For every test required in the "Tests" tab (e.g. Test 1), please provide the completed the PSCAD plots on the coresponding test plots tab ( e.g. Test 1 Plots). Plots should include:
Machine Active Power (MW)
Machine Reactive Power (MVARs)
POI Voltage (p.u.)
POI Frequency (Hz)
If there are multiple energy resources (e.g. PV / Wind plus BESS), MW/MVARs for each should be plotted in separate channels
4 | Refer to ATC Planning Methodology Document PLG-PRD-0017 for detailed instructions on how to complete each item in this checklist.

## Usability
PSCAD Plant Model Usability Requirements
Item # | Requirement | Interconnection Customer/Generator Owner Comment | ATC Comment
1 | The manufacturer’s name and the specific version of the inverter model should be clearly observable in the .psc model file.
2 | PSCAD model instructional documentation should be provided and should match the model version in the .psc model file and include instructions for setup and running of the model.
3 | Model uses a simulation timestep of 10 µs or larger.
4 | Model compiles using Intel FORTRAN version 15 or higher.
5 | Model uses PSCAD version 4.6 or higher.
6 | Model supports the PSCAD “snapshot” feature.
7 | Model supports the PSCAD “multiple run” feature.
8 | Model can be scaled to represent any number inverters/turbines, either using a scaling transformer or internal scaling. Model should not be using current injection to scale the plant.
9 | Model includes power plant controller (PPC)
10 | PPC accepts an external active power setpoint.
11 | PPC accepts a voltage setpoint of 1.02 p.u. at POI. PPC is in voltage control mode.
12 | PPC has a mechanism to implement a settable voltage droop.
13 | 60 Hz grid frequency base

## PSSE-PSCAD Parameter Comparison
PSSE Plant Model parameters vs PSCAD Plant Model parameters Verification
Item # | Equipment | Parameter | PSSE Model/MISO DPP Application | PSCAD Plant Model
1 | Generator | Energy Resource Interconnection Service (ERIS) MW level requested at the Point of Interconection (POI)
Total Machine MVA (Mbase)
Inverter Voltage
# of inverters that make up the generator
2 | Generator Step Up Transformer (Inverter to Medium Voltage) | GSU Low voltage winding kV
GSU Low voltage winding configuration
GSU High voltage winding kV
GSU High voltage winding configuration
Transformer MVA
Copper losses (R based on the MVA of the transformer)
Positive Sequence Leakage Reactance (X based on the MVA of the transformer)
3 | Equivalent Collector Branch | R (p.u.)
X (p.u.)
B (p.u.)
4 | Main Power Transformer (Medium Voltage to POI Voltage) | MPT Low voltage winding kV
MPT Low voltage winding configuration
MPT High voltage winding kV
MPT High voltage winding configuration
Transformer MVA
Copper losses (R based on the MVA of the transformer)
Positive Sequence Leakage Reactance (X based on the MVA of the transformer)
5 | Gen Tie Line | R (p.u.)
X (p.u.)
B (p.u.)
6 | Cap Banks | # of banks
MVAR of banks
Connection bus
Cap bank dispatch control scheme
7 | Dynamic Voltage Control Devices | MVAR rating
connection bus
8 | Aux load included (if greater than 1 MW) | MW
MVAR
connection bus
9 | Protection Settings | Will the plant have AC overcurrent protection enabled? | N/A
|  | If yes, is the AC overcurent protection enabled in the PSCAD plant model? | N/A
|  | Will the plant have DC protection enabled? | N/A
|  | If yes, is the DC protection enabled in the PSCAD plant model? | N/A
Over Voltage 1: Voltage Setting (p.u.)
Over Voltage 1: Time Setting (sec)
Over Voltage 2: Voltage Setting (p.u.)
Over Voltage 2: Time Setting (sec)
Over Voltage 3: Voltage Setting (p.u.)
Over Voltage 3: Time Setting (sec)
Over Voltage 4: Voltage Setting (p.u.)
Over Voltage 4: Time Setting (sec)
Over Voltage 5: Voltage Setting (p.u.)
Over Voltage 5: Time Setting (sec)
Under Voltage 1: Voltage Setting (p.u.)
Under Voltage 1: Time Setting (sec)
Under Voltage 2: Voltage Setting (p.u.)
Under Voltage 2: Time Setting (sec)
Under Voltage 3: Voltage Setting (p.u.)
Under Voltage 3: Time Setting (sec)
Under Voltage 4: Voltage Setting (p.u.)
Under Voltage 4: Time Setting (sec)
Under Voltage 5: Voltage Setting (p.u.)
Under Voltage 5: Time Setting (sec)
Over Frequency 1: Voltage Setting (Hz)
Over Frequency 1: Time Setting (sec)
Over Frequency 2: Voltage Setting (Hz)
Over Frequency 2: Time Setting (sec)
Over Frequency 3: Voltage Setting (Hz)
Over Frequency 3: Time Setting (sec)
Over Frequency 4: Voltage Setting (Hz)
Over Frequency 4: Time Setting (sec)
Over Frequency 5: Voltage Setting (Hz)
Over Frequency 5: Time Setting (sec)
Under Frequency 1: Voltage Setting (Hz)
Under Frequency 1: Time Setting (sec)
Under Frequency 2: Voltage Setting (Hz)
Under Frequency 2: Time Setting (sec)
Under Frequency 3: Voltage Setting (Hz)
Under Frequency 3: Time Setting (sec)
Under Frequency 4: Voltage Setting (Hz)
Under Frequency 4: Time Setting (sec)
Under Frequency 5: Voltage Setting (Hz)
Under Frequency 5: Time Setting (sec)

## Tests
PSCAD Plant Model Tests
Item # | Test | Requirement | Interconnection Customer/Generator Owner Comment | ATC Comment
1 | Flat Run Test | Model initializes to PPC setpoints in 5 seconds Meet ATC Planning Criteria
2 | 3PG Fault at 100% of MW Test | Plant cap banks must be dispatched and the plant must meet ATC Planning Criteria
3 | 1PG Fault at 100% of MW Test | Plant cap banks must be dispatched and the plant must meet ATC Planning Criteria
4 | 3PG Fault at 20% of MW Test | Plant cap banks must be dispatched and the plant must meet ATC Planning Criteria
5 | 1PG Fault at 20% of MW Test | Plant cap banks must be dispatched and the plant must meet ATC Planning Criteria
6 | 3PG Fault test Charging | Plant cap banks must be dispatched and the plant must meet ATC Planning Criteria
7 | 1PG Fault test Charging | Plant cap banks must be dispatched and the plant must meet ATC Planning Criteria
8 | System Strength Test | Plant cap banks must be dispatched and the plant must meet ATC Planning Criteria for an appropriate SCR
9 | Over Frequency Step Test | Meet ATC Planning Criteria
10 | Voltage Step Test | Meet ATC Planning Criteria
11 | Over Voltage Protection Test | Plant should trip
12 | Under Voltage Protection Test | Plant should trip
13 | Under Voltage Dynamic Response Test | Meet ATC Planning Criteria
14 | NERC PRC-024-3 Test | Plant should not trip or enter momentary cessation Meet ATC Planning Criteria